Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, low power usage and easy to use.

16 Port DI Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators. The DIP switch for Slave ID and Baud rate are placed inside the enclosure.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against sudden High Voltage spikes. the board also has ‘reverse polarity’ protection both for input and power connector.

the communication port also has signal isolation and additional jumper for ‘end of line’120 ohms termination resistance which may or may not be used.

Specifications

General –

I/O Connectors		2 Pin 5.08 mm pitch pluggable screw Terminal Block

Dimensions			110 mm L x 110 mm B x 50mm H

Power			Input Power – 24 V AC/DC

Typical – 12V DC @ 110mA

Operating Temperature	0 – 60° C (32 ~ 140°F)

Storage Temperature	-20 - 70° C (-4 ~ 158°F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DI Inputs –

Channels			16

Sense Voltage 		4 – 40 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

Additional Features: -

Power input and communication port is isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2, ± 30KV contact, ± 30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

DIP SETTING – For Manual Switch Setup

Configuration Settings: -

Communication Speed 	9600 – 115200 Kbps (DIP SW selectable)

Data Bits			8

Parity 			None

CRC				Yes

Stop bit			1

Slave ID			DIP SW selectable (1-15)

Function code DI		0x02 Read discrete Input

DI Register Address	0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | DI 1(With & Without Potential) | 10001 | 0X02 | RS485 | 1 Bit Boolean |
| 2 | DI 2(With & Without Potential) | 10002 | 0X02 | RS485 | 1 Bit Boolean |
| 3 | DI 3(With & Without Potential) | 10003 | 0X02 | RS485 | 1 Bit Boolean |
| 4 | DI 4(With & Without Potential) | 10004 | 0X02 | RS485 | 1 Bit Boolean |
| 5 | DI 5(With & Without Potential) | 10005 | 0X02 | RS485 | 1 Bit Boolean |
| 6 | DI 6(With & Without Potential) | 10006 | 0X02 | RS485 | 1 Bit Boolean |
| 7 | DI 7(With & Without Potential) | 10007 | 0X02 | RS485 | 1 Bit Boolean |
| 8 | DI 8(With & Without Potential) | 10008 | 0X02 | RS485 | 1 Bit Boolean |
| 9 | DI 9(With & Without Potential) | 10009 | 0X02 | RS485 | 1 Bit Boolean |
| 10 | DI 10(With & Without Potential) | 10010 | 0X02 | RS485 | 1 Bit Boolean |
| 11 | DI 11(With & Without Potential) | 10011 | 0X02 | RS485 | 1 Bit Boolean |
| 12 | DI 12(With & Without Potential) | 10012 | 0X02 | RS485 | 1 Bit Boolean |
| 13 | DI 13(With & Without Potential) | 10013 | 0X02 | RS485 | 1 Bit Boolean |
| 14 | DI 14(With & Without Potential) | 10014 | 0X02 | RS485 | 1 Bit Boolean |
| 15 | DI 15(With & Without Potential) | 10015 | 0X02 | RS485 | 1 Bit Boolean |
| 16 | DI 16(With & Without Potential) | 10016 | 0X02 | RS485 | 1 Bit Boolean |

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

BAUD RATE DESCRIPTION

LSB

MSB

- For Baud rate Selection, DIP SW is used as per the diagram.

- Pulling up the switch will make Baud rate active.

- If no selection is made 9600 will be default Baud rate.

- When u change the Baud rate in the Module power ‘ON’ condition,

pls press the reset button to get Change to affect.

| Baud Rate | DIP SWITCH |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |
| 9600 | OFF | OFF | OFF | OFF |
| 19200 | ON | OFF | OFF | OFF |
| 38400 | OFF | ON | OFF | OFF |
| 57600 | OFF | OFF | ON | OFF |
| 115200 | OFF | OFF | OFF | ON |

SLAVE ID DESCRIPTION

MSB

LSB

For Slave ID Selection SW is used to Set the SLAVE ID .

For Slave ID DIP Switch LSB is “1” follow through “4” is MSB.

Slave ID Confirmed through below Device ID table .

IF Eg. Slave ID 1 is Needed to be selected Switch number 1 should pulled up other three should be selected down side. So”1 0 0 0” will be selected as Slave ID 1.

| Slave ID | DIP SWITCH |  |  |  | OUTPUT (Binary) | OUTPUT (Decimal) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |  |  |
| 0 | OFF(0) | OFF(0) | OFF(0) | OFF(0) | 1 0 0 0 | 1 |
| 1 | ON(1) | OFF(0) | OFF(0) | OFF(0) | 1 0 0 0 | 1 |
| 2 | OFF(0) | ON(1) | OFF(0) | OFF(0) | 0 1 0 0 | 2 |
| 3 | ON(1) | ON(1) | OFF(0) | OFF(0) | 1 1 0 0 | 3 |
| 4 | OFF(0) | OFF(0) | ON(1) | OFF(0) | 0 0 1 0 | 4 |
| 5 | ON(1) | OFF(0) | ON(1) | OFF(0) | 1 0 1 0 | 5 |
| 6 | OFF(0) | ON(1) | ON(1) | OFF(0) | 0 1 1 0 | 6 |
| 7 | ON(1) | ON(1) | ON(1) | OFF(0) | 1 1 1 0 | 7 |
| 8 | OFF(0) | OFF(0) | OFF(0) | ON(1) | 1 0 0 0 | 8 |
| 9 | ON(1) | OFF(0) | OFF(0) | ON(1) | 1 0 0 1 | 9 |
| 10 | OFF(0) | ON(1) | OFF(0) | ON(1) | 1 0 1 0 | 10 |
| 11 | ON(1) | OFF(0) | ON(1) | ON(1) | 1 0 1 1 | 11 |
| 12 | OFF(0) | OFF(0) | ON(1) | ON(1) | 1 1 0 0 | 12 |
| 13 | ON(1) | OFF(0) | ON(1) | ON(1) | 1 1 0 1 | 13 |
| 14 | OFF(0) | ON(1) | ON(1) | ON(1) | 1 1 1 0 | 14 |
| 15 | ON(1) | ON(1) | ON(1) | ON(1) | 1 1 1 1 | 15 |

SOFT SETTING – For Modbus / Software Setup

Configuration Settings: -

Communication Speed 	      9600 – 115200 (DIP SW selectable)

Data Bits			      8

Parity 			      None

Stop bit			     1

CRC				     Yes

Slave ID			     Soft settings (0-255).

Function code DI		     0x02 Read Discrete coil

DI Register Address	     0, 1, 2, 3, 4, 5, 6, 7,8,9,10,11,12,13,14,15.

Note:

- In register 40015- you will be able to see the current parity and you can change it in register 40016

- In register 40017- you will be able to see the current stop bit and you can change it in register 40018

- If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it as 960/1920/5760/11520etc.

- After that press the reset button or reboot the system

BAUD RATE and SLAVE ID DESCRIPTION:

- As you can see in the image above, the resistor 40011 – 960 represents the present bund rate (9600) of the board and 40013 – 1 represents the present slave id of the board.

- To change the baud rate and slave id you must enter a value on the 40012, resistor for the baud rate and 40014 for the slave id as shown in the image below.

As you can see in the image above I set 115200 baud rate and slave ID 25.

Note:

- When entering baud rate values such as 9600 / 19200 / 38400 / 57600 / 115200, enter them as 960 / 1920 / 3840 / 5760 / 11520, respectively.

- After entering the values, press the reset button or reboot the system.

- Once restarted, you will see the updated values:

- 40011 – 11520 → Baud Rate (115200)

- 40013 – 25 → Slave ID (25)

- You can also change Parity Bit and Stop Bit of the device in the same way.

- Jumper Setting (Hardware Method):

- If you place the jumper, the device will load its default communication settings (default baud rate (9600) and slave ID (1)).

- This is useful when you have many devices with different settings and want a quick way to restore   defaults without software changes.

- Relation between Jumper and Reset Button:
 The jumper enables the default mode, and the reset button activates it.

- Simply insert the jumper → press reset → the device restarts with factory default settings     automatically

8   7   6   5   4   3     2   1

DI +ve terminal Pins

9 10  11 12  13 14 15 16

DI +ve terminal Pins

Modbus RS485

Input 24 V AC / DC

Common GND

Common GND

Ref

12 VDC

Ref

12 VDC

MSB

MSB

LSB

LSB

Slave ID

Baud Rate

Note: http://www.youtube.com/@wittelb

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805