Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, low power usage and easy to use.

4 Port DO + 4 DI  Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against reverse polarity connection both for Power and Communication port.

Specification

General –

I/O Connectors	12 Pin 5.08 mm pitch pluggable screw Terminal Block, 2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions			110 mm L x 110 mm B x 50 mm H

Power			Input Power – 12 - 24 VDC or 24 V AC/DC

Typical – 12V DC @ 120mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DO with Relay Output –

Channels			4

Contact Form		1A, 1C

Contact Material		Ag Alloy

Contact Capacity		10A @ 240VAC, 10A @ 28VDC

Coil Voltage			5 – 48 VDC

Coil Power			0.36 W

Insulation Resistance	250M

Electrical Life		1 x 10^5

Mechanical Life		1 x 10^7

Operating Time 		7 msec, Max 15 msec

Release Time		2 msec, Max 6 msec

DI Inputs –

Channels			4

Sense Voltage 		3.3 – 30 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 0 | DO1 | 00001 | 0X02 | RS485 | 1 Bit Boolean |
| 1 | DO2 | 00002 | 0X02 | RS485 | 1 Bit Boolean |
| 2 | DO3 | 00003 | 0X02 | RS485 | 1 Bit Boolean |
| 3 | DO4 | 00004 | 0X02 | RS485 | 1 Bit Boolean |
| 4 | DI 1(With & Without Potential) | 10005 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 5 | DI 1(With & Without Potential) | 10006 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 6 | DI 1(With & Without Potential) | 10007 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 7 | DI 1(With & Without Potential) | 10008 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 10 | Display Baud Rate (Default:960) | 40011 | 0x03 | RS485 | 16 Bit Unsigned int |
| 11 | Enter New Baud Rate | 40012 | 0x03 | RS485 | 16 Bit Unsigned int |
| 12 | Display Slave ID (Default:1) | 40013 | 0x03 | RS485 | 16 Bit Unsigned int |
| 13 | Enter New Slave ID | 40014 | 0x03 | RS485 | 16 Bit Unsigned int |
| 14 | Display Parity (Default: None-3, Odd- 1, Even-2) | 40015 | 0x03 | RS485 | 16 Bit Unsigned int |
| 15 | Enter New Parity | 40016 | 0x03 | RS485 | 16 Bit Unsigned int |
| 16 | Display Stop Bit (start-2/stop bit-1) | 40017 | 0x03 | RS485 | 16 Bit Unsigned int |
| 17 | Enter New Start/ Stop Bit | 40018 | 0x03 | RS485 | 16 Bit Unsigned int |

Configuration Settings: -

Communication Speed 	9600 – 115200

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Function code DO		0x05 and 0x0F (5 Single coil & 15 multiple coil)

DO Register Address	0,1,2,3.

Function code DI		0x02 Read discrete Input

DI Register Address	4,5,6,7.

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

Additional Features: -

All inputs  and communication ports isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Note:

- In register 40015- you will be able to see the current parity and you can change it in register 40016

- In register 40017- you will be able to see the current stop bit and you can change it in register 40018

- If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it as 960/1920/5760/11520etc.

- After that press the reset button or reboot the system.

As you can see in the image above, the resistor 40011 – 960 represents the present bund rate (9600) of the board and 40013 – 1 represents the present slave id of the board.

To change the baud rate and slave id you have to enter a value on the 40012 registor for the baud rate and 40014 for the slave id as shown in the image below.

As you can see in the image above I set 115200 baud rate and slave ID 25.

Note:

1. If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it like this 960/1920/5760/11520etc.

2. After that press the reset button or reboot the system.

3. Then you will get the present value of 11520 at 40011 baud rate(115200) and 25 at 40013 slave id.

4.  You can Change Parity Bit , stop bit Of the device with same way.

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

DO

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

- Digital Output (DO) operation: Each channel provides two terminals: C (Common) and NO (Normally Open). When the relay coil is energized, terminal C is internally connected to NO, allowing current to flow. When the relay is de-energized, the connection between C and NO remains open, and the load stays OFF.

- Load Wiring Connections:

  - AC Load Connection: The AC Live (Phase) wire should be connected to terminal C. The load is connected between terminal NO and Neutral (N).

  - DC Load Connection: The positive supply (+V) should be connected to terminal C. The load is connected between terminal NO and Ground (GND).

- Crucial Safety Recommendation and Rating: It is strongly recommended to switch the Live (Phase) conductor in AC applications to ensure the load is safely de-energized when the relay is off.

Note: Ensure that the connected load does not exceed the relay’s contact rating of 10A @ 250VAC (or 10A @ 125VAC) or 10A @ 30VDC (or 10A @ 28VD

4       3        2       1

DO- NO Contacts

1   2   3   4

DI +ve Pins

Modbus RS485

Input 12-24    VDC

Common GNDD

+12 V DI Ref

Contact Information

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support E.: support@wittelb.raiseaticket.com  / M.: 9403892805