Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, low power usage and easy to use.

4 Port DO + 4 DI + 4 AI Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators. The DIP switch for Slave ID and Baud rate are placed inside the enclosure.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against reverse polarity connection both for Power and Communication port.

Specifications

General –

I/O Connectors	14 Pin 5.08 mm pitch pluggable screw Terminal Block,

Dimensions			110 mm L x 110 mm B x 50 mm H

Power			Input Power – 12 - 24 VDC or 24 V AC/DC

Typical – 12V DC @ 120mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DI Inputs –

Channels			4

Sense Voltage 		3.3 – 30 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

AI Inputs –

Channels			4

Input Signal			4 – 20 mA / 0 – 10VDC / NTC Type 3 (jumper selectable)

Accuracy			 2% Full scale

Input Resolution		10 bits / 12 bits (Optional)

Isolation			Optically Isolated

External Loop Voltage	+ 12 VDC min

AI input impedance 	120

Additional Features: -

All inputs  and communication ports isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Configuration Settings: -

Communication Speed 	9600 – 115200 (DIP SW selectable)

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID			Configurable with DIP Switch

Function code DI		0x02 Read discrete Input

DI Register Address	0,1,2,3.

Function Code AI		0x03 Read Holding Registers

AI Register Address	10 Bit - 2,3,4,5 / 12 Bit – 6,7,8,9.

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | DI 1(With & Without Potential) | 10001 | 0X02 | RS485 | 1 Bit Boolean |
| 2 | DI 2(With & Without Potential) | 10002 | 0X02 | RS485 | 1 Bit Boolean |
| 3 | DI 3(With & Without Potential) | 10003 | 0X02 | RS485 | 1 Bit Boolean |
| 4 | DI 4(With & Without Potential) | 10004 | 0X02 | RS485 | 1 Bit Boolean |
| 5 | AI 1 – 10 Bit | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 6 | AI 2 – 10 Bit | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 7 | AI 3 – 10 Bit | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 8 | AI 4 – 10 Bit | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 9 | AI – 1 12 Bit | 40006 | 0x03 | RS485 | 16 Bit Unsigned int |
| 10 | AI – 2 12 Bit | 40007 | 0x03 | RS485 | 16 Bit Unsigned int |
| 11 | AI – 3 12 Bit | 40008 | 0x03 | RS485 | 16 Bit Unsigned int |
| 12 | AI – 4 12 Bit | 40009 | 0x03 | RS485 | 16 Bit Unsigned int |

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

AI

Sensor

Sensor

Sensor

Sensor

- Analog Input (AI) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to read external analog sensor signals.

- Channel Configuration (Visual Guide): Each of the four AI channels features two dedicated jumpers to independently set the voltage range and bit resolution. Refer to the color-coded boxes in the board diagram to configure your desired scenario:

  - Red Box (5V, 10-bit): Set the voltage jumper to +5V and the resolution jumper to 10 BIT.

  - Green Box (5V, 12-bit): Set the voltage jumper to +5V and the resolution jumper to 12 BIT.

  - Blue Box (10V, 10-bit): Set the voltage jumper to +10V and the resolution jumper to 10 BIT.

  - Yellow Box (10V, 12-bit): Set the voltage jumper to +10V and the resolution jumper to 12 BIT.

- Sensor Wiring Connections:

  - The analog sensor's positive signal wire should be connected to the + terminal of the desired channel.

  - The sensor's common or ground wire should be connected to the corresponding - terminal.

- Crucial Setup Recommendation: Always ensure that the voltage jumper setting strictly matches the maximum output range of your connected sensor (either 5V or 10V) to guarantee accurate analog-to-digital conversion and prevent data clipping.

SLAVE ID DESCRIPTION

MSB

LSB

For Slave ID Selection SW is used to Set The SLAVE ID .

For Slave ID DIP Switch LSB is “1” follow through “4” is MSB.

Slave ID Confirmed through below Device ID table .

IF Eg. Slave ID 1 is Needed to be selected Switch number 1 should pulled up other three should be selected down side. So”1 0 0 0” will be selected as Slave ID 1.

| Slave ID | DIP SWITCH |  |  |  | OUTPUT (Binary) | OUTPUT (Decimal) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |  |  |
| 0 | OFF(0) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 1 | ON(1) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 2 | OFF(0) | ON(1) | OFF(0) | OFF(0) | 0 0 1 0 | 2 |
| 3 | ON(1) | ON(1) | OFF(0) | OFF(0) | 0 0 1 1 | 3 |
| 4 | OFF(0) | OFF(0) | ON(1) | OFF(0) | 0 1 0 0 | 4 |
| 5 | ON(1) | OFF(0) | ON(1) | OFF(0) | 0 1 0 1 | 5 |
| 6 | OFF(0) | ON(1) | ON(1) | OFF(0) | 0 1 1 0 | 6 |
| 7 | ON(1) | ON(1) | ON(1) | OFF(0) | 0 1 1 1 | 7 |
| 8 | OFF(0) | OFF(0) | OFF(0) | ON(1) | 1 0 0 0 | 8 |
| 9 | ON(1) | OFF(0) | OFF(0) | ON(1) | 1 0 0 1 | 9 |
| 10 | OFF(0) | ON(1) | OFF(0) | ON(1) | 1 0 1 0 | 10 |
| 11 | ON(1) | ON(1) | OFF(0) | ON(1) | 1 0 1 1 | 11 |
| 12 | OFF(0) | OFF(0) | ON(1) | ON(1) | 1 1 0 0 | 12 |
| 13 | ON(1) | OFF(0) | ON(1) | ON(1) | 1 1 0 1 | 13 |
| 14 | OFF(0) | ON(1) | ON(1) | ON(1) | 1 1 1 0 | 14 |
| 15 | ON(1) | ON(1) | ON(1) | ON(1) | 1 1 1 1 | 15 |

1   2   3   4

DI +ve Pins

AI4    AI3    AI2   AI1

Analog Input Pins

MSB

LSB

SLAVE ID

Modbus RS485

Input 12-24    VDC

Common GNDD

+12 V DI Ref

5V / 10 V

AI Jumper

10 / 12 Bit

AI Jumper

Contact Information

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support E.: support@wittelb.raiseaticket.com  / M.: 9403892805