Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, low power usage and easy to use.

# Port AI Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators. The DIP switch for Slave ID and Baud rate are placed inside the enclosure.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against sudden High Voltage spikes. The board also has ‘reverse polarity’ protection both for input Power connector.

The communication port also has signal isolation and additional Jumper for ‘end of line’ 120 ohms termination resistance which may or may not be used.

# Specifications

## General

I/O Connectors 	2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions  	                      70 mm L x 110 mm B x 50 mm H

Power 	 	                      Input Power – 12 – 24 VDC

Typical – 12V DC @ 1 Amp

Operating Temperature  0 – 60 C (32 ~ 140F)

| Storage Temperature | -20 - 70 C (-4 ~ 158F)) |
| --- | --- |
| Storage Humidity | 5 ~ 95 % RH, non – Condensing |

Certifications

| AI Inputs – |  |
| --- | --- |
| Channels | 8 |
| Input Signal | 0 - 75 mV |
| Accuracy | 2 % of Full scale |
| Input Resolution | 10-bit /12-bit resolution (optional) |
| Isolation | Optically Isolated |
| AI input impedance | 120 |

## Additional Features: -

Communication port isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV airEFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

## Configuration Settings: -

Communication Speed    9600 – 19200 Kbps (DIP SW Selectable)

| Data Bits |  |  | 8 |
| --- | --- | --- | --- |
| Parity |  |  | None |
| Stop bit |  |  | 1 |
| CRC |  |  | Yes |
| Slave ID |  |  | 1 – 15 (DIP SW Selectable) |

Function Code AI  	0x09 Read Holding Registers

AI Register Address 	10 Bit - 0,1,2,3,4,5,6,7 / 12 Bit – 8,9,10,11,12,13,14,15

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | AI 1 – 10 Bit | 40001 | 0X03 | RS485 | 16 Bit Unsigned int |
| 2 | AI 2 – 10 Bit | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 3 | AI 3 – 10 Bit | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 4 | AI 4 – 10 Bit | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 5 | AI 5 – 10 Bit | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 6 | AI 6 – 10 Bit | 40006 | 0X03 | RS485 | 16 Bit Unsigned int |
| 7 | AI 7 – 10 Bit | 40007 | 0X03 | RS485 | 16 Bit Unsigned int |
| 8 | AI 8 – 10 Bit | 40008 | 0X03 | RS485 | 16 Bit Unsigned int |
| 9 | AI – 1 12 Bit | 40009 | 0x03 | RS485 | 16 Bit Unsigned int |
| 10 | AI – 2 12 Bit | 40010 | 0x03 | RS485 | 16 Bit Unsigned int |
| 11 | AI – 3 12 Bit | 40011 | 0x03 | RS485 | 16 Bit Unsigned int |
| 12 | AI – 4 12 Bit | 40012 | 0x03 | RS485 | 16 Bit Unsigned int |
| 13 | AI – 5 12 Bit | 40013 | 0x03 | RS485 | 16 Bit Unsigned int |
| 14 | AI – 6 12 Bit | 40014 | 0x03 | RS485 | 16 Bit Unsigned int |
| 15 | AI – 7 12 Bit | 40015 | 0x03 | RS485 | 16 Bit Unsigned int |
| 16 | AI – 8 12 Bit | 40016 | 0x03 | RS485 | 16 Bit Unsigned int |

## Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

## Recommended Cable Electrical Characteristics: -

22 AWG Cable  	 	                                Shielded and twisted pair should be used.

Tinned Copper 	 	                                Recommended

Nominal Conductor DCR                       14.7 ohm / 1000 ft

Nominal Capacitance 	                            11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss 	0.5db / 100ft

NOTE – By default the Jumper setting on the board is 10 V and 10 Bit.

BAUD RATE DESCRIPTION

L

SB

M

SB

- For Baud rate Selection, DIP SW is used as per the diagram.

- Pulling up the switch will make Baud rate active.

- If no selection is made 9600 will be default Baud rate.

- When u change the Baud rate in the Module power ‘ON’ condition,  please press the reset button to get Change to affect.

| Baud Rate | DIP SWITCH |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |
| 9600 | OFF | OFF | OFF | OFF |
| 115200 | ON | OFF | OFF | OFF |
| 57600 | OFF | ON | OFF | OFF |
| 38400 | OFF | OFF | ON | OFF |
| 19200 | OFF | OFF | OFF | ON |

### SLAVE ID DESCRIPTION

MSB

LSB

For Slave ID Selection SW is used to Set The SLAVE ID .

For Slave ID DIP Switch LSB is “1” follow through “4” is MSB.

Slave ID Confirmed through below Device ID table .

IF Eg. Slave ID 1 is Needed to be selected Switch number 1 should pulled up other three should be selected down side. So”1 0 0 0” will be selected as Slave ID 1.

| Slave ID | DIP SWITCH |  |  |  | OUTPUT (Binary) | OUTPUT (Decimal) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |  |  |
| 0 | OFF(0) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 1 | ON(1) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 2 | OFF(0) | ON(1) | OFF(0) | OFF(0) | 0 0 1 0 | 2 |
| 3 | ON(1) | ON(1) | OFF(0) | OFF(0) | 0 0 1 1 | 3 |
| 4 | OFF(0) | OFF(0) | ON(1) | OFF(0) | 0 1 0 0 | 4 |
| 5 | ON(1) | OFF(0) | ON(1) | OFF(0) | 0 1 0 1 | 5 |
| 6 | OFF(0) | ON(1) | ON(1) | OFF(0) | 0 1 1 0 | 6 |
| 7 | ON(1) | ON(1) | ON(1) | OFF(0) | 0 1 1 1 | 7 |
| 8 | OFF(0) | OFF(0) | OFF(0) | ON(1) | 1 0 0 0 | 8 |
| 9 | ON(1) | OFF(0) | OFF(0) | ON(1) | 1 0 0 1 | 9 |
| 10 | OFF(0) | ON(1) | OFF(0) | ON(1) | 1 0 1 0 | 10 |
| 11 | ON(1) | ON(1) | OFF(0) | ON(1) | 1 0 1 1 | 11 |
| 12 | OFF(0) | OFF(0) | ON(1) | ON(1) | 1 1 0 0 | 12 |
| 13 | ON(1) | OFF(0) | ON(1) | ON(1) | 1 1 0 1 | 13 |
| 14 | OFF(0) | ON(1) | ON(1) | ON(1) | 1 1 1 0 | 14 |
| 15 | ON(1) | ON(1) | ON(1) | ON(1) | 1 1 1 1 | 15 |

Input Device

AI

Input Device

- Analog Input (AI) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to read external analog sensor signals.

- Channel Configuration (Visual Guide): Each of the four AI channels features dedicated jumper to independently set the 10 & 12bit resolution:

  - Red & Blue Box (10-bit): Set the resolution jumper to 10 BIT resolution.

  - Green & Yellow Box (12-bit): Set the resolution jumper to 12 BIT resolution.

- Sensor Wiring Connections:

  - DC Shunt/ Load’s should be connected to the + terminal of the desired channel.

  - DC Shunt/ Load’s should be connected to the - terminal.

MSB

MSB

Slave ID

LSB

LSB

Baud Rate

10/12 Bit Jumper

Selectable

10/12 Bit Jumper

Selectable

Power LED

Polling LED

RS 485

24V DC

AI8      |      AI7     |      AI6    |     AI5

AI1      |      AI2     |      AI3    |     AI4

Contact Information

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support E.: support@wittelb.raiseaticket.com  / M.: 9403892805