Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, has low power usage and is easy to use.

8 DI + 8 AI – NTC Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against reverse polarity connection both for Power and Communication port.

Specifications

General –

I/O Connectors	12 Pin 5.08 mm pitch pluggable screw Terminal Block, 2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions			110 mm L x 110 mm B x 50 mm H

Power			Input Power – 12 - 24 VDC or 24 V AC/DC

Typical – 12V DC @ 120mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DI Inputs –

Channels			8

Sense Voltage 		3.3 – 30 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

AI Inputs –

Channels			8

Input Signal			4 – 20 mA / 0 – 10VDC / NTC Type 3 (jumper selectable)

Accuracy			 2% Full scale

Input Resolution		10 bits / 12 bits (Optional)

Isolation			Optically Isolated

External Loop Voltage	+ 12 VDC min

AI input impedance 	120

Additional Features: -

All inputs  and communication ports isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Configuration Settings: -

Communication Speed 	         9600 – 115200.

Data Bits			         8

Parity 			         None

Stop bit			         1

CRC				         Yes

Slave Id                                        Soft Setting

Function code DI		         0x02 Read discrete Input

DI Register Address	         0,1,2,3,4,5,6,7,8.

Function Code AI		         0x03 Read Holding Registers

AI Register Address	         10 Bit - 1,2,3,4,5,6,7,8

Soft Serial Function Code         0x03 Read Holding Registers

Soft Serial Register Address    11,12,13,14,15,16,17,18.

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 0 | DI 1(With & Without Potential) | 10001 | 0X02 | RS485 | 1 Bit Boolean |
| 1 | DI 2(With & Without Potential) | 10002 | 0X02 | RS485 | 1 Bit Boolean |
| 2 | DI 3(With & Without Potential) | 10003 | 0X02 | RS485 | 1 Bit Boolean |
| 3 | DI 4(With & Without Potential) | 10004 | 0X02 | RS485 | 1 Bit Boolean |
| 4 | DI 5(With & Without Potential) | 10005 | 0x02 | RS485 | 1 Bit Boolean |
| 5 | DI 6(With & Without Potential) | 10006 | 0x02 | RS485 | 1 Bit Boolean |
| 6 | DI 7(With & Without Potential) | 10007 | 0x02 | RS485 | 1 Bit Boolean |
| 7 | DI 8(With & Without Potential) | 10008 | 0x02 | RS485 | 1 Bit Boolean |
| 1 | AI 1 – 10 Bit | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 2 | AI 2 – 10 Bit | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 3 | AI 3 – 10 Bit | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 4 | AI 4 – 10 Bit | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 5 | AI 5 – 10 Bit | 40006 | 0x03 | RS485 | 16 Bit Unsigned int |
| 6 | AI 6 – 10 Bit | 40007 | 0x03 | RS485 | 16 Bit Unsigned int |
| 7 | AI 7 – 10 Bit | 40008 | 0x03 | RS485 | 16 Bit Unsigned int |
| 8 | AI 8 – 10 Bit | 40009 | 0x03 | RS485 | 16 Bit Unsigned int |
| 9 | Temperature1 | 40010 | 0x03 | RS485 | 16 Bit Unsigned int |
| 10 | Temperature2 | 40011 | 0x03 | RS485 | 16 Bit Unsigned int |
| 11 | Temperature3 | 40012 | 0x03 | RS485 | 16 Bit Unsigned int |
| 12 | Temperature4 | 40013 | 0x03 | RS485 | 16 Bit Unsigned int |
| 13 | Temperature5 | 40014 | 0x03 | RS485 | 16 Bit Unsigned int |
| 14 | Temperature6 | 40015 | 0x03 | RS485 | 16 Bit Unsigned int |
| 15 | Temperature7 | 40016 | 0x03 | RS485 | 16 Bit Unsigned int |
| 16 | Temperature8 | 40017 | 0x03 | RS485 | 16 Bit Unsigned int |
| 18 | Display Baud Rate (Default:960) | 40019 | 0x03 | RS485 | 16 Bit Unsigned int |
| 19 | Enter New Baud Rate | 40020 | 0x03 | RS485 | 16 Bit Unsigned int |
| 20 | Display Slave ID (Default:1) | 40021 | 0x03 | RS485 | 16 Bit Unsigned int |
| 21 | Enter New Slave ID | 40022 | 0x03 | RS485 | 16 Bit Unsigned int |
| 22 | Display Parity (Default: None-3And for Odd-1,Even-2 | 40023 | 0x03 | RS485 | 16 Bit Unsigned int |
| 23 | Enter New Parity | 40024 | 0x03 | RS485 | 16 Bit Unsigned int. |
| 24 | Display Stop Bit (start-2/stop bit-1) | 40025 | 0x03 | RS485 | 16 Bit Unsigned int. |
| 25 | Enter New Start/ Stop Bit. | 40026 | 0x03 | RS485 | 16 Bit Unsigned int. |

Note: -

- In register 40023- you will be able to see the current parity and you can change it to register 40024

- In register 40025- you will be able to see the current stop bit, and you can change it in register 40026

- If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it as 960/1920/5760/11520etc.

- After that press the reset button or reboot the system.

BAUD RATE and SLAVE ID DESCRIPTION:

As you can see in the image above, the resistor 40019 – 960 represents the present bund rate

(9600) of the board and 40021– 1 represents the present slave id of the board.

To change the baud rate and slave id you have to enter a value on the 40020 resistor for the baud rate and 40022 for the slave id as shown in the image below.

As you can see in the image above I set 115200 baud rate and slave ID 5.

Note:

1. If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it like this 960/1920/5760/11520etc.

2. After that press the reset button or reboot the system.

3. Then you will get the present value of 11520 at 40019 baud rate(115200) and 5 at 40021 slave id.

4.  You can Change Parity Bit , stop bit Of the device with same way.

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

AI-NTC

Sensor

Sensor

Sensor

Sensor

- Analog Input & NTC Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to interface with either standard external analog sensors or NTC thermistors.

- Channel Configuration (Visual Guide): Each of the four channels features two dedicated jumpers to independently select the operating mode (AI or NTC) and the reference voltage range (5V or 10V). Refer to the color-coded boxes in the board diagram to configure your desired scenario:

  - Red Box (AI Mode, 5V Range): Set the mode jumper to AI and the voltage jumper to +5V.

  - Green Box (AI Mode, 10V Range): Set the mode jumper to AI and the voltage jumper to +10V.

  - Blue Box (NTC Mode, 5V Range): Set the mode jumper to NTC and the voltage jumper to +5V.

  - Yellow Box (NTC Mode, 10V Range): Set the mode jumper to NTC and the voltage jumper to +10V.

- Sensor Wiring Connections:

  - The sensor or thermistor's positive signal wire should be connected to the + terminal of the desired channel (labelled AI1/NTC, AI2/NTC, etc.).

  - The sensor's common or ground wire should be connected to the corresponding - terminal.

- Crucial Setup Recommendation: Always ensure that both the mode jumper (NTC vs. AI) and the voltage jumper strictly match the hardware you are connecting. Incorrectly setting an NTC to an AI mode, or mismatching the voltage limits, will result in inaccurate temperature or signal readings.

BAUD RATE DESCRIPTION

Default Setting

DIP switch

NOTE –

- By default, the Jumper setting on the board is 10 V and 10 Bit.

- By default, Baud rate DIP Switch 1 is set to ON, toggling it OFF and pressing reset button will bring the device to default RS485 Configuration i.e.  Baud rate - 9600, Stop bit - 1, Parity - None, Data Bit - 8. Keep the indicated DIP switch to ON position for setting desired configuration.

1     2    3     4    5     6     7    8

DI +ve Pins

Common GNDD

Modbus RS485

DIP

SWITCH

FOR

BAUDRATE

& SLAE ID

AI | NTC SELECT

5V / 10 V

Jumper

Input 12-24    VDC

AI8       AI7        AI6       AI5       AI4       AI3        AI2        AI1

Analog Input Pins

+12 V DI Ref

Reset Button

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi, Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805