Technical Datasheet 4G Gateway with 5DI, 4DO, & 2AI

Product Overview: -

The 4G Gateway is an advanced networking device designed to provide seamless connectivity and data management capabilities for various applications. With support for 4G LTE connectivity, cloud connectivity via MQTT protocol, and robust storage options, it offers a comprehensive solution for remote monitoring and control systems. Equipped with an integrated I/O interface featuring 5 Digital Inputs (DI), 4 Digital Outputs (DO), and 2 Analog Inputs (AI), alongside a Modbus RS485 port and micro SIM compatibility, it caters to a wide range of industrial and IoT applications. The intuitive web-based UI interface allows for easy configuration and management, making it an ideal choice for both professionals and enthusiasts.

Specifications

General:-

- 4G LTE + GNSS Connectivity: Utilizes 4G LTE technology for reliable and high-speed internet access. If 4G is not available, the system automatically switches to Wi-Fi. If both 4G and Wi-Fi are unavailable, the data is securely stored in the SD card for later upload. It also supports GPS.

- Cloud Connectivity (MQTT): Seamlessly connects to cloud platforms using the MQTT protocol for efficient data transmission and management.

- Event Storage: Offers on board event storage, capable of storing up to 50,000 events or more. Includes an external memory card slot for easy data retrieval in the event of 4G network issues.

- Modbus RS485 Port: Features 1 port of Modbus RS485 for integration with industrial control systems and sensors.

- GPS Location Data: Provides GPS location data for monitoring of remote equipment.

- Micro Sim Compatibility: Supports micro-Sim card for flexible and convenient connectivity option.

- Web-based UI Interface: Intuitive web-based user interface for easy configuration, monitoring, and management.

- Dimensions: 110 mm L x 110 mm B x 50 mm H.

- Power: Input Power – 15-40 VDC, Typical – 12V DC @ 150mA.

- Operating Temperature: 0 – 60C (32 ~ 140F).

- Storage Temperature: 20 - 70C (-4 ~ 158F).

- Storage Humidity: 5 ~ 95 % RH, non – Condensing.

Configuration Settings: -

- Power up the module by connecting a 12-24 V DC supply.

- Insert the SIM card into the designated slot.

- Place the Micro SD card into its designated slot.

- Connect MODBUS RTU Multiple Slave devices (up to 31) to the A & B Terminal

Of Module.

- Access the module's configuration hotspot

(ID: Wittelb-4G-GATEWAY, PASS: 123456789).

- Default IP Address of Module is “192.168.1.100/cpp1”.

- Upon entering the provided IP address, a configuration  webpage

Pages will be accessible.

Page1:-

- Enter Device ID (Should be unique for every device).

- Enter data frequency in min to receive data on cloud.

- Enter time to upload SD card data to cloud.

Page2:- On second page you can set device Baud Rate (9600 / 19200 / 38400 /   57600 / 115200), Data Bits (5 / 6 / 7 / 8), Parity (None / Odd / Even), and Stop Bits (1 / 2) for RS485 Communication

Page3:-

      - Navigate to page 3 on the cloud platform.

      - Input the Host IP or Domain.

      - Enter the port Number.

      - Enter the topics for publishing and receiving messages.

      - Provide a username and password if required.

      - Allow a few seconds for the module to restart and establish a connection to MQTT.

Page4:-

- Go to page 4 on the Modbus Master interface.

- Input the name and slave address for the designated slave.

- Specify the register address from which you want to read slave data.

- Indicate the register end address for the slave.

- Enter the function code corresponding to the desired slave.

Page5:-

- Go to page 5 on the I/O Config interface.

- You can view real-time values of both analog and digital inputs on the baseboard.

- Additionally, you have the option to assign specific names to each input/output

(I/O) as needed.

Page6:-

- Navigate to page 6 on the Logical Operations interface.

- Here, you can configure logical AND and OR operations for each of the 4 relays.

- You have the flexibility to assign any two digital inputs to a relay and choose the desired logical operation.

- Additionally, you can assign an analog input to a relay and define minimum and maximum threshold values for relay operation.

- If you prefer not to use any logical operation, simply select the "OFF" option for

input one.

Relay Logical Operation — Formula & Usage Guide: -

## 1. Overview

Each relay (Relay 1 - Relay 4) can be configured with up to 2 conditions — Condition 1 (required) and Condition 2 (optional). A condition can be based on a Digital Input (DI) or an Analog Input (AI). If both conditions are used, they are combined using AND / OR logic. The final result (TRUE/FALSE) determines whether the relay turns ON or OFF.

## 2. Digital Input (DI) Condition

Formula:

Condition = TRUE, if DI_value == Expected_state

Expected_state: HIGH = 1, LOW = 0

Available channels: DI1 – DI6

## 3. Analog Input (AI) Condition

The raw value of an AI channel is first converted into a percentage (%), then compared against a threshold percentage.

Formula 1 — Raw value to Percentage:

AI_Percent (%) = ( Raw_Value / Max_Raw ) × 100

Max_Raw (resolution) is FIXED per channel — the user does not select it:

| AI Channel | Resolution | Max Raw Value | Source |
| --- | --- | --- | --- |
| AI1, AI2 | 10-bit | 1023 | Onboard ESP32 ADC |
| AI3, AI4 | 12-bit | 4095 | External ADC (MCP) |

Formula 2 — Percentage to Condition:

Direction = "above"  →  Condition = TRUE, if AI_Percent ≥ Threshold_%

Direction = "below"  →  Condition = TRUE, if AI_Percent ≤ Threshold_%

## 4. Combining the Two Conditions (AND / OR)

If Condition 2 is set (input2Type ≠ NONE), the final result is:

Final_Result = Condition1  AND  Condition2      (when Logic = AND — both must be TRUE)

Final_Result = Condition1  OR  Condition2       (when Logic = OR — either one being TRUE is enough)

If only Condition 1 is set (Condition 2 = NONE):

Final_Result = Condition1

AND / OR Truth Table:

| Condition 1 | Condition 2 | AND Result | OR Result |
| --- | --- | --- | --- |
| TRUE | TRUE | TRUE | TRUE |
| TRUE | FALSE | FALSE | TRUE |
| FALSE | TRUE | FALSE | TRUE |
| FALSE | FALSE | FALSE | FALSE |

AND → Relay turns ON only when BOTH conditions are TRUE at the same time.

OR → Relay turns ON when AT LEAST ONE condition is TRUE.

## 5. Relay Output

Final_Result = TRUE   →  Relay ON  (command: aiN:1)

Final_Result = FALSE  →  Relay OFF (command: aiN:0)

This check repeats approximately every 500 ms (400 ms poll + 100 ms delay), so the relay continuously follows live input conditions.

## 6. Example

Relay 1 Setup: Condition 1 = AI3 above 60%  |  Logic = AND  |  Condition 2 = DI1 HIGH

AI3 raw reading = 3000 (12-bit, Max_Raw = 4095)

AI_Percent = (3000 / 4095) × 100 = 73.26%

73.26% ≥ 60% → Condition1 = TRUE

DI1 value = 1 (HIGH) → Condition2 = TRUE

Final_Result = TRUE AND TRUE = TRUE → Relay 1 turns ON

## 7. How to Configure (Web Page)

1. Connect to the gateway's Access Point and open the "Logical Operations" page (cpp10) in a browser.

2. For each Relay, select the Condition 1 type (DI or AI).

3. If DI is selected, choose the channel and the HIGH/LOW state.

4. If AI is selected, choose the channel, Threshold %, and Direction (above/below). Resolution is fixed automatically based on the channel.

5. If a second condition is needed, set the Logic (AND/OR) and configure Condition 2; otherwise leave Condition 2 = NONE.

6. Click "Save Relay" — the configuration is applied immediately.

4G Gateway connection Diagram:

Power   And

Connection to baseboard

RS485 & Polling

Led

Power &

Network

Led

Sim Card Slot

SD Card Slot

Modbus [A-B]

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805