Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO module communicates via Ethernet Interface. The module is designed to allow interface with other Modbus TCP/IP compatible devices. The module acts as an input/output device between the Modbus TCP/IP Network and the Gateway.

Digital IO module is sturdy, low power usage and easy to use.

4 Port DO + 4 DI + 4 AI Module with Modbus TCP Ethernet: -

The IO modules enclosures are DIN rail Mountable. It’s a closed Enclosure with openings for connectors and LED indicators.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against reverse polarity connection for Power Input.

There are LED indicators for each of the IO ports as well as for the module Power.

Specifications

General –

I/O Connectors	22 Pin 5.08 mm pitch pluggable screw Terminal Block, 2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions			110 mm L x 110 mm B x 50 mm H

Power			Input Power – 12-24 V DC

Typical – 12V DC @ 120mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DO with Relay Output –

Channels			4

Contact Form		1A, 1C

Contact Material		Ag Alloy

Contact Capacity		10A @ 240VAC, 10A @ 28VDC

Coil Voltage			5 – 48 VDC

Coil Power			0.36 W

Insulation Resistance	250M

Electrical Life		1 x 10^5

Mechanical Life		1 x 10^7

Operating Time 		7 msec, Max 15 msec

Release Time		2 msec, Max 6 msec

DI Inputs –

Channels			4

Sense Voltage 		3.3 – 30 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

AI Inputs –

Channels			4

Input Signal			4 – 20 mA / 0 – 10VDC / NTC Type 3 (jumper selectable)

Accuracy			 2% Full scale

Input Resolution		10 bits / 12 bits (Optional)

Isolation			Optically Isolated

External Loop Voltage	+ 12 VDC min

AI input impedance 	120

Configuration Settings: -

Communication Speed 	10/100 Base-T Ethernet Interface

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID			Configurable over Web Interface

Function code DO		0x05 and 0x0F (5 Single coil & 15 multiple coil)

DO Register Address	4,5,6,7.

Function code DI		0x02 Read discrete Input

DI Register Address	0,1,2,3.

Function Code AI		0x03 Read Holding Registers

AI Register Address	10 Bit - 2,3,4,5 / 12 Bit – 6,7,8,9.

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | DO 1 | 00001 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 2 | DO 2 | 00002 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 3 | DO 3 | 00003 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 4 | DO 4 | 00004 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 5 | DI 1(With & Without Potential) | 10005 | 0X02 | RS485 | 1 Bit Boolean |
| 6 | DI 2(With & Without Potential) | 10006 | 0X02 | RS485 | 1 Bit Boolean |
| 7 | DI 3(With & Without Potential) | 10007 | 0X02 | RS485 | 1 Bit Boolean |
| 8 | DI 4(With & Without Potential) | 10008 | 0X02 | RS485 | 1 Bit Boolean |
| 9 | AI 1 – 10 Bit | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 10 | AI 2 – 10 Bit | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 11 | AI 3 – 10 Bit | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 12 | AI 4 – 10 Bit | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 13 | AI 1 – 12 Bit | 40006 | 0x03 | RS485 | 16 Bit Unsigned int |
| 14 | AI 2 – 12 Bit | 40007 | 0x03 | RS485 | 16 Bit Unsigned int |
| 15 | AI 3 – 12 Bit | 40008 | 0x03 | RS485 | 16 Bit Unsigned int |
| 16 | AI 4 – 12 Bit | 40009 | 0x03 | RS485 | 16 Bit Unsigned int |

## Configuration Guide – Ethernet Modbus TCP/IP IO Module:-

- Open a web browser (Google Chrome, Microsoft Edge, Firefox, etc.).

- In the browser’s address bar, type the default IP address:
      192.168.0.160

- Press Enter. A message will appear saying:
      “Please go to http://192.168.0.160/setup.”

- Copy this link (http://192.168.0.160/setup) and paste it into a new browser tab.

- Press Enter again to open the Setup / Configuration Page of the device.

## To Reset the Device to Default Settings

- Place the jumper on the designated Reset position on the device.

- Press the Reset button once.

- The module will reboot and revert to its default IP address: 192.168.0.160.

## To Change the IP Address

- On the Setup / Configuration Page, enter the new IP address you wish to assign.

- Click Submit to save the new settings.

- The device will automatically apply the new IP address.

Note:

- Ensure your PC’s IP address is in the same network range (for example,       192.168.0.xxx) when accessing the module.

- After changing the IP, you must use the new address to log in again.

4DDAME

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

DO

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

- Digital Output (DO) operation: Each channel provides two terminals: C (Common) and NO (Normally Open). When the relay coil is energized, terminal C is internally connected to NO, allowing current to flow. When the relay is de-energized, the connection between C and NO remains open, and the load stays OFF.

- Load Wiring Connections:

  - AC Load Connection: The AC Live (Phase) wire should be connected to terminal C. The load is connected between terminal NO and Neutral (N).

  - DC Load Connection: The positive supply (+V) should be connected to terminal C. The load is connected between terminal NO and Ground (GND).

- Crucial Safety Recommendation and Rating: It is strongly recommended to switch the Live (Phase) conductor in AC applications to ensure the load is safely de-energized when the relay is off.

Note: Ensure that the connected load does not exceed the relay’s contact rating of 10A @ 250VAC (or 10A @ 125VAC) or 10A @ 30VDC (or 10A @ 28VDC).

AI

Sensor

Sensor

Sensor

Sensor

- Analog Input (AI) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to read external analog sensor signals.

- Channel Configuration (Visual Guide): Each of the four AI channels features two dedicated jumpers to independently set the voltage range and bit resolution. Refer to the color-coded boxes in the board diagram to configure your desired scenario:

  - Red Box (5V, 10-bit): Set the voltage jumper to +5V and the resolution jumper to 10 BIT.

  - Green Box (5V, 12-bit): Set the voltage jumper to +5V and the resolution jumper to 12 BIT.

  - Blue Box (10V, 10-bit): Set the voltage jumper to +10V and the resolution jumper to 10 BIT.

  - Yellow Box (10V, 12-bit): Set the voltage jumper to +10V and the resolution jumper to 12 BIT.

- Sensor Wiring Connections:

  - The analog sensor's positive signal wire should be connected to the + terminal of the desired channel.

  - The sensor's common or ground wire should be connected to the corresponding - terminal.

- Crucial Setup Recommendation: Always ensure that the voltage jumper setting strictly matches the maximum output range of your connected sensor (either 5V or 10V) to guarantee accurate analog-to-digital conversion and prevent data clipping.

Product Image:

DO Ports

1        2        3        4

GD   4    3    2     1 +12V

DI +ve Pins

AI   I/P

AI1      AI2

Input 24    VDC

5V / 10 V

AI Jumper

10 / 12 Bit

AI Jumper

Modbus TCP Ethernet

AI4      AI3

AI I/p

Note – Configuration Guide is separately provided for the configuration of the module.

For more details: http://www.youtube.com/@wittelb

Contact Information

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805