32 channel NPN based DO

The IO modules communicate via RS485. The port can drive distances up to max 200 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, has low power usage and is easy to use.

32 Port DO Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators. Baud rate and slave ID can be changed by software setting.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against reverse polarity connection both for Power and Communication port.

Specifications

General –

I/O Connectors		5.08 mm pitch pluggable screw Terminal Block

Dimensions			157 mm L x 110 mm B x 73 mm H

Power			Input Power –24 V DC options

Typical – 12V DC @ 150mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Output mode                     Collector NPN output

Response speed                0.01 seconds (10ms)
Application design          Industrial-grade anti-interference design, stable

Certifications

Additional Features: -

Communication ports are isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

400V isolation.

CRC Error check.

No configuration needed on the IO board

Configuration Settings: -

Communication Speed 	9600 – 115200 Kbps (Software selectable)

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID			Software selectable

Function code		0x01

DO Register Address	0 to 31

| ID | Function | Register | Protocol | Data |
| --- | --- | --- | --- | --- |
|  | Description | Description |  | Type |
| 1 | DO 1 | 1 | RS485 | 1 Bit Boolean |
| 2 | DO 2 | 2 | RS485 | 1 Bit Boolean |
| 3 | DO 3 | 3 | RS485 | 1 Bit Boolean |
| 4 | DO 4 | 4 | RS485 | 1 Bit Boolean |
| 5 | DO 5 | 5 | RS485 | 1 Bit Boolean |
| 6 | DO 6 | 6 | RS485 | 1 Bit Boolean |
| 7 | DO 7 | 7 | RS485 | 1 Bit Boolean |
| 8 | DO 8 | 8 | RS485 | 1 Bit Boolean |
| 9 | DO 9 | 9 | RS485 | 1 Bit Boolean |
| 10 | DO 10 | 10 | RS485 | 1 Bit Boolean |
| 11 | DO 11 | 11 | RS485 | 1 Bit Boolean |
| 12 | DO 12 | 12 | RS485 | 1 Bit Boolean |
| 13 | DO 13 | 13 | RS485 | 1 Bit Boolean |
| 14 | DO 14 | 14 | RS485 | 1 Bit Boolean |
| 15 | DO 15 | 15 | RS485 | 1 Bit Boolean |
| 16 | DO 16 | 16 | RS485 | 1 Bit Boolean |
| 17 | DO 17 | 17 | RS485 | 1 Bit Boolean |
| 18 | DO 18 | 18 | RS485 | 1 Bit Boolean |
| 19 | DO 19 | 19 | RS485 | 1 Bit Boolean |
| 20 | DO 20 | 20 | RS485 | 1 Bit Boolean |
| 21 | DO 21 | 21 | RS485 | 1 Bit Boolean |
| 22 | DO 22 | 22 | RS485 | 1 Bit Boolean |
| 23 | DO 23 | 23 | RS485 | 1 Bit Boolean |
| 24 | DO 24 | 24 | RS485 | 1 Bit Boolean |
| 25 | DO 25 | 25 | RS485 | 1 Bit Boolean |
| 26 | DO 26 | 26 | RS485 | 1 Bit Boolean |
| 27 | DO 27 | 27 | RS485 | 1 Bit Boolean |
| 28 | DO 28 | 28 | RS485 | 1 Bit Boolean |
| 29 | DO 29 | 29 | RS485 | 1 Bit Boolean |
| 30 | DO 30 | 30 | RS485 | 1 Bit Boolean |
| 31 | DO 31 | 31 | RS485 | 1 Bit Boolean |
| 32 | DO 32 | 32 | RS485 | 1 Bit Boolean |

DO

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

- Digital Output (DO) operation: Each channel provides two terminals: C (Common) and NO (Normally Open). When the relay coil is energized, terminal C is internally connected to NO, allowing current to flow. When the relay is de-energized, the connection between C and NO remains open, and the load stays OFF.

- Load Wiring Connections:

  - AC Load Connection: The AC Live (Phase) wire should be connected to terminal C. The load is connected between terminal NO and Neutral (N).

  - DC Load Connection: The positive supply (+V) should be connected to terminal C. The load is connected between terminal NO and Ground (GND).

- Crucial Safety Recommendation and Rating: It is strongly recommended to switch the Live (Phase) conductor in AC applications to ensure the load is safely de-energized when the relay is off.

Note: Ensure that the connected load does not exceed the relay’s contact rating of 10A @ 250VAC (or 10A @ 125VAC) or 10A @ 30VDC (or 10A @ 28VDC).

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded Twisted pair should be used

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100f

Application design as above

This is default Modbus setting that is Baud rate is 9600, Slave ID is 1.

Baud rate is multiple of 10(960*10=9600)

To change baud rate and slave ID , at the selectable register the required value of Baud rate and Slave ID, Make a power cycle (Power ON/OFF the product) and Connect Modbus with changed parameters.

DIGITAL OUTPUT (DO) (MOSFET)

17|18|19|20|21|22|23|24|25|26|27|28|29|30|31|32

16|15|14|13|12|11|10|09|08|07|06|05|04|03|02|01

DIGITAL OUTPUT (DO) (MOSFET)

Common

GND

12/24V DC

Inut Supply

MODBUS

RS485

Polling

LED

RESET

DIP Switch: Baud rate & Slave ID

Power

LED

Default Setting

Common

GND

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805