Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

The IO modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital IO module is sturdy, low power usage and easy to use.

4 DI + 3 DO + 4 AI + 2 AO Module: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators. The DIP switch for Slave ID and Baud rate are placed inside the enclosure.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against sudden High Voltage spikes. the board also has ‘reverse polarity’ protection both for input and power connector.

the communication port also has signal isolation and additional jumper for ‘end of line’120 ohms termination resistance which may or may not be used.

Specifications

General –

I/O Connectors	12 Pin 5.08 mm pitch pluggable screw Terminal Block, 2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions			110 mm L x 110 mm B x 50 mm H

Power			Input Power – 12 - 24 VDC or 24 V AC/DC

Typical – 12V DC @ 120mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DO with Relay Output –

Channels			3

Contact Form		1A, 1C

Contact Material		Ag Alloy

Contact Capacity		10A @ 240VAC, 10A @ 28VDC

Coil Voltage			5 – 48 VDC

Coil Power			0.36 W

Insulation Resistance	250M

Electrical Life		1 x 10^5

Mechanical Life		1 x 10^7

Operating Time 		7 msec, Max 15 msec

Release Time		2 msec, Max 6 msec

DI Inputs –

Channels			4

Sense Voltage 		3.3 – 30 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

AI Inputs –

Channels			4

Input Signal			4 – 20 mA / 0 – 10VDC / NTC Type 3 (jumper selectable)

Accuracy			 2% Full scale

Input Resolution		10 bits / 12 bits (Optional)

Isolation			Optically Isolated

External Loop Voltage	+ 12 VDC min

AI input impedance 	120

AO Outputs –

Channels			2

Inputs Resolution		10 Bit (12 Bit Optional)

Signal Range		0 – 10V

Accuracy			 2 % of Full scale

Linearity Error		0.1 %

Conversion Time		20 msec

Additional Features: -

All inputs and communication ports isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

Configuration Settings: -

Communication Speed 	9600 – 115200 (DIP SW selectable)

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID			Configurable with DIP Switch

Function code DO		0x05 and 0x0F (5 Single coil & 15 multiple coil)

DO Register Address	0,1,2.

Function code DI		0x02 Read discrete Input

DI Register Address	3,4,5,6.

Function Code AI		0x03 Read Holding Registers

AI Register Address	10 Bit – 1,2,3,4.

Function Code AO		0x03 Read Holding Registers

AO Register Address	10 Bit – 5,6.

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | DO 1 | 00001 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 2 | DO 2 | 00002 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 3 | DO 3 | 00003 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 4 | DI 1(With & Without Potential) | 10004 | 0X02 | RS485 | 1 Bit Boolean |
| 5 | DI 2(With & Without Potential) | 10005 | 0X02 | RS485 | 1 Bit Boolean |
| 6 | DI 3(With & Without Potential) | 10006 | 0X02 | RS485 | 1 Bit Boolean |
| 7 | DI 4(With & Without Potential) | 10007 | 0X02 | RS485 | 1 Bit Boolean |
| 8 | AI 1 – 10 Bit | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 9 | AI 2 – 10 Bit | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 10 | AI 3 – 10 Bit | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 11 | AI 4 – 10 Bit | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 12 | AO 1 – 10 Bit | 40006 | 0x03 | RS485 | 16 Bit Unsigned int |
| 13 | AO 2 – 10 Bit | 40007 | 0x03 | RS485 | 16 Bit Unsigned int |

AI

Sensor

Sensor

Sensor

Sensor

- Analog Input (AI) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to read external analog sensor signals.

- Channel Configuration (Visual Guide): Each of the four AI channels features two dedicated jumpers to independently set the voltage range and bit resolution. Refer to the color-coded boxes in the board diagram to configure your desired scenario:

  - Red Box (5V, 10-bit): Set the voltage jumper to +5V and the resolution jumper to 10 BIT.

  - Green Box (5V, 12-bit): Set the voltage jumper to +5V and the resolution jumper to 12 BIT.

  - Blue Box (10V, 10-bit): Set the voltage jumper to +10V and the resolution jumper to 10 BIT.

  - Yellow Box (10V, 12-bit): Set the voltage jumper to +10V and the resolution jumper to 12 BIT.

- Sensor Wiring Connections:

  - The analog sensor's positive signal wire should be connected to the + terminal of the desired channel.

  - The sensor's common or ground wire should be connected to the corresponding - terminal.

- Crucial Setup Recommendation: Always ensure that the voltage jumper setting strictly matches the maximum output range of your connected sensor (either 5V or 10V) to guarantee accurate analog-to-digital conversion and prevent data clipping.

AO

O/p device

O/p device

O/p device

- Analog Output (AO) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to send variable analog signals to external output (O/p) devices, such as variable frequency drives or proportional valves.

- Channel Configuration (Visual Guide): Each of the three AO channels features a dedicated jumper to set the output bit resolution. Refer to the color-coded boxes in the board diagram to configure your desired resolution:

  - Green & Yellow Box (12-bit): Set the resolution jumper to 12Bit.

  - Blue Box (10-bit): Set the resolution jumper to 10Bit.

- Output Device Wiring Connections:

  - The external device's positive signal wire should be connected to the + terminal of the desired channel (AO1, AO2, or AO3).

  - The device's common or ground wire should be connected to the corresponding - terminal..

- Crucial Setup Recommendation: Always ensure that the hardware jumper setting (10-bit or 12-bit) matches the output scaling configured in your main control software. A mismatch between software resolution and hardware configuration will result in incorrect output signal levels.

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

DO

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

- Digital Output (DO) operation: Each channel provides two terminals: C (Common) and NO (Normally Open). When the relay coil is energized, terminal C is internally connected to NO, allowing current to flow. When the relay is de-energized, the connection between C and NO remains open, and the load stays OFF.

- Load Wiring Connections:

  - AC Load Connection: The AC Live (Phase) wire should be connected to terminal C. The load is connected between terminal NO and Neutral (N).

  - DC Load Connection: The positive supply (+V) should be connected to terminal C. The load is connected between terminal NO and Ground (GND).

- Crucial Safety Recommendation and Rating: It is strongly recommended to switch the Live (Phase) conductor in AC applications to ensure the load is safely de-energized when the relay is off.

Note: Ensure that the connected load does not exceed the relay’s contact rating of 10A @ 250VAC (or 10A @ 125VAC) or 10A @ 30VDC (or 10A @ 28VDC).

BAUD RATE DESCRIPTION

MSB

LSB

- For Baud rate Selection, DIP SW is used as per the diagram.

- Pulling up the switch will make Baud rate active.

- If no selection is made 9600 will be default Baud rate.

- When u change the Baud rate in the Module power ‘ON’ condition,

please press the reset button to get Change to affect.

| Baud Rate | DIP SWITCH |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |
| 9600 | OFF | OFF | OFF | OFF |
| 19200 | ON | OFF | OFF | OFF |
| 38400 | OFF | ON | OFF | OFF |
| 57600 | OFF | OFF | ON | OFF |
| 115200 | OFF | OFF | OFF | ON |

SLAVE_ID_DESCRIPTION

MSB

LSB

- For Slave ID Selection SW is used to Set the SLAVE ID

- For Slave ID DIP Switch LSB is “1” follow through “4” is MSB.

- Slave ID Confirmed through below Device ID table.

- IF Eg: Slave ID 1 is Needed to be selected Switch number 1 should pulled up other three should be selected down side. So”1 0 0 0” will be selected as Slave ID 1.

| Slave ID | DIP SWITCH |  |  |  | OUTPUT (Binary) | OUTPUT (Decimal) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |  |  |
| 0 | OFF(0) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 1 | ON(1) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 2 | OFF(0) | ON(1) | OFF(0) | OFF(0) | 0 0 1 0 | 2 |
| 3 | ON(1) | ON(1) | OFF(0) | OFF(0) | 0 0 1 1 | 3 |
| 4 | OFF(0) | OFF(0) | ON(1) | OFF(0) | 0 1 0 0 | 4 |
| 5 | ON(1) | OFF(0) | ON(1) | OFF(0) | 0 1 0 1 | 5 |
| 6 | OFF(0) | ON(1) | ON(1) | OFF(0) | 0 1 1 0 | 6 |
| 7 | ON(1) | ON(1) | ON(1) | OFF(0) | 0 1 1 1 | 7 |
| 8 | OFF(0) | OFF(0) | OFF(0) | ON(1) | 1 0 0 0 | 8 |
| 9 | ON(1) | OFF(0) | OFF(0) | ON(1) | 1 0 0 1 | 9 |
| 10 | OFF(0) | ON(1) | OFF(0) | ON(1) | 1 0 1 0 | 10 |
| 11 | ON(1) | ON(1) | OFF(0) | ON(1) | 1 0 1 1 | 11 |
| 12 | OFF(0) | OFF(0) | ON(1) | ON(1) | 1 1 0 0 | 12 |
| 13 | ON(1) | OFF(0) | ON(1) | ON(1) | 1 1 0 1 | 13 |
| 14 | OFF(0) | ON(1) | ON(1) | ON(1) | 1 1 1 0 | 14 |
| 15 | ON(1) | ON(1) | ON(1) | ON(1) | 1 1 1 1 | 15 |

SOFT_SETTING – For Modbus / Software Setup

Configuration Settings: -

Communication Speed 	      9600 – 115200 (DIP SW selectable)

Data Bits			      8

Parity 			      None

Stop bit			      1

CRC				      Yes

Slave ID			      Soft settings (1-247).

Function code DO		      0x05 and 0x0F (5 Single coil & 15 multiple coil)

DO Register Address	      0, 1, 2.

Function code DI                     0x02 Read Discrete Input

Function Code Soft Serial      0x03 Read Holding Registers

DI Register Address	3,4,5,6.

AI Register Address                 1,2,3,4.

AO Register Address               5,6.

Note:

- In register 40015- you will be able to see the current parity and you can change it in register 40016

- In register 40017- you will be able to see the current stop bit and you can change it in register 40018

- If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it as 960/1920/5760/11520etc.

- After that press the reset button or reboot the system.

BAUD RATE and SLAVE ID DESCRIPTION:

- As you can see in the image above, the resistor 40011 – 960 represents the present bund rate (9600) of the board and 40013 – 1 represents the present slave id of the board.

- To change the baud rate and slave id you have to enter a value on the 40012, resistor for the baud rate and 40014 for the slave id as shown in the image below.

As you can see in the image above I set 115200 baud rate and slave ID 25.

Note:

- When entering baud rate values such as 9600 / 19200 / 38400 / 57600 / 115200, enter them as 960 / 1920 / 3840 / 5760 / 11520, respectively.

- After entering the values, press the reset button or reboot the system.

- Once restarted, you will see the updated values:

- 40011 – 11520 → Baud Rate (115200)

- 40013 – 25 → Slave ID (25)

- You can also change Parity Bit and Stop Bit of the device in the same way.

- Jumper Setting (Hardware Method):

- If you place the jumper, the device will load its default communication settings (default baud rate (9600) and slave ID (1)).

- This is useful when you have many devices with different settings and want a quick way to restore   defaults without software changes.

- Relation between Jumper and Reset Button:
 The jumper enables the default mode, and the reset button activates it.

- Simply insert the jumper → press reset → the device restarts with factory default settings     automatically

1       2       3

DO – NO contact

4   3   2   1

DI +ve Pins

AI4    AI3    AI2   AI1

Analog Input Pins

MSB

LSB

SLAVE ID

Modbus RS485

Input 12-24    VDC

Common GNDD

+12 V DI Ref

5V / 10 V

AI Jumper

AI / NTC

AI Jumper

1       2

AO(0-10v)

BAUD Rate

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805