Technical Datasheet Input / Output Modules with Modbus TCP Protocol with Ethernet Interface

The IO module communicates via Ethernet Interface. The module is designed to allow interface with other Modbus TCP/IP compatible devices. The module acts as an input/output device between the Modbus TCP/IP Network and the Gateway.

Digital IO module is sturdy, low power usage and easy to use.

# 8 Port AI Module with Modbus TCP Ethernet Port: -

The IO modules are mounted on DIN rail mountable casing and with exposed connectors and LED indicators.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against sudden High Voltage spikes. The board also has ‘reverse polarity’ protection both for input Power connector.

The communication port also has signal isolation and additional Jumper for ‘end of line’ 120 ohms termination resistance which may or may not be used.

# Specifications

## General: –

I/O Connectors 	2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions  	 	70 mm L x 70 mm B x 50 mm H

Power 	 	 	Input Power – 12 – 24 VDC or 24 V AC/DC

Typical – 12V DC @ 1Amp

Operating Temperature    0 – 60 C (32 ~ 140F)

| Storage Temperature | -20 - 70 C (-4 ~ 158F) |
| --- | --- |
| Storage Humidity | 5 ~ 95 % RH, non – Condensing |

Certifications

| AI Inputs: – |  |
| --- | --- |
| Channels | 8 |
| Input Signal | 4 – 20 mA / 0 – 20 mA / 0 – 10 V (jumper selectable) |
| Accuracy | 2 % of Full scale |
| Input Resolution | 10-bit /12-bit resolution (optional) |
| Isolation | Optically Isolated |
| External Loop Voltage | + 12 VDC min |
| AI input impedance | 120 |

## Additional Features: -

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

Web based Configuration needed for the IO board

## Configuration Settings: -

Communication Speed     10/100 Base-T Ethernet compatible Interface

Function Code AI  	0x03 Read Holding Registers

AI Register Address           	10 Bit - 0,1,2,3,4,5,6,7 / 12 Bit – 8, 9,10,11,12,13,14,15

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | AI 1 – 10 Bit | 40001 | 0X03 | RS485 | 16 Bit Unsigned int |
| 2 | AI 2 – 10 Bit | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 3 | AI 3 – 10 Bit | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 4 | AI 4 – 10 Bit | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 5 | AI 5 – 10 Bit | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 6 | AI 6 – 10 Bit | 40006 | 0X03 | RS485 | 16 Bit Unsigned int |
| 7 | AI 7 – 10 Bit | 40007 | 0X03 | RS485 | 16 Bit Unsigned int |
| 8 | AI 8 – 10 Bit | 40008 | 0X03 | RS485 | 16 Bit Unsigned int |
| 9 | AI – 1 12 Bit | 40009 | 0x03 | RS485 | 16 Bit Unsigned int |
| 10 | AI – 2 12 Bit | 40010 | 0x03 | RS485 | 16 Bit Unsigned int |
| 11 | AI – 3 12 Bit | 40011 | 0x03 | RS485 | 16 Bit Unsigned int |
| 12 | AI – 4 12 Bit | 40012 | 0x03 | RS485 | 16 Bit Unsigned int |
| 13 | AI – 5 12 Bit | 40013 | 0x03 | RS485 | 16 Bit Unsigned int |
| 14 | AI – 6 12 Bit | 40014 | 0x03 | RS485 | 16 Bit Unsigned int |
| 15 | AI – 7 12 Bit | 40015 | 0x03 | RS485 | 16 Bit Unsigned int |
| 16 | AI – 8 12 Bit | 40016 | 0x03 | RS485 | 16 Bit Unsigned int |

## Note: -

## For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

## Recommended Cable Electrical Characteristics: -

22 AWG Cable  	                                  	Shielded and twisted pair should be used.

Tinned Copper 	 		Recommended

Nominal Conductor DCR        			14.7 ohm / 1000 ft

Nominal Capacitance 	                                   11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss 	0.5db / 100ft

## Configuration Guide – Ethernet Modbus TCP/IP IO Module:-

- Open a web browser (Google Chrome, Microsoft Edge, Firefox, etc.).

- In the browser’s address bar, type the default IP address:
      192.168.0.160

- Press Enter. A message will appear saying:
      “Please go to http://192.168.0.160/setup.”

- Copy this link (http://192.168.0.160/setup) and paste it into a new browser tab.

- Press Enter again to open the Setup / Configuration Page of the device.

## To Reset the Device to Default Settings

- Place the jumper on the designated Reset position on the device.

- Press the Reset button once.

- The module will reboot and revert to its default IP address: 192.168.0.160.

## To Change the IP Address

- On the Setup / Configuration Page, enter the new IP address you wish to assign.

- Click Submit to save the new settings.

- The device will automatically apply the new IP address.

Note:

- Ensure your PC’s IP address is in the same network range (for example,       192.168.0.xxx) when accessing the module.

- After changing the IP, you must use the new address to log in again.

AI

Sensor

Sensor

Sensor

Sensor

- Analog Input (AI) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to read external analog sensor signals.

- Channel Configuration (Visual Guide): Each of the four AI channels features two dedicated jumpers to independently set the voltage range and bit resolution. Refer to the color-coded boxes in the board diagram to configure your desired scenario:

  - Red Box (5V, 10-bit): Set the voltage jumper to +5V and the resolution jumper to 10 BIT.

  - Green Box (5V, 12-bit): Set the voltage jumper to +5V and the resolution jumper to 12 BIT.

  - Blue Box (10V, 10-bit): Set the voltage jumper to +10V and the resolution jumper to 10 BIT.

  - Yellow Box (10V, 12-bit): Set the voltage jumper to +10V and the resolution jumper to 12 BIT.

- Sensor Wiring Connections:

  - The analog sensor's positive signal wire should be connected to the + terminal of the desired channel.

  - The sensor's common or ground wire should be connected to the corresponding - terminal.

- Crucial Setup Recommendation: Always ensure that the voltage jumper setting strictly matches the maximum output range of your connected sensor (either 5V or 10V) to guarantee accurate analog-to-digital conversion and prevent data clipping.

AI

4

AI

3

AI

2

AI

1

AI

5

AI

6

AI

7

AI

8

Input

12

-

24

VDC

Modbus

TCP

Ethernet

Jumper

V / 10V

5

Jumper

/ 12

10

Bit

Jumper

10

/ 12

Bit

Jumper

V / 10V

5

NOTE:–

By default, the Jumper setting on the board is 10 V and 10 Bit.

## Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805