Technical Datasheet Input / Output Modules with Modbus TCP Protocol with Ethernet Interface

The IO module communicates via Ethernet Interface. The module is designed to allow interface with other Modbus TCP/IP compatible devices. The module acts as an input/output device between the Modbus TCP/IP Network and the Gateway.

Digital IO module is sturdy, has low power usage and is easy to use.

Port DO Module with Modbus TCP Ethernet : -

The IO modules enclosures are DIN rail Mountable. It’s a closed Enclosure with openings for connectors and LED indicators.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against sudden High Voltage spikes. the board also has ‘reverse polarity’ protection both for input and power connector.

the communication port also has signal isolation and additional jumper for ‘end of line’120 ohms termination resistance which may or may not be used.

Specifications

General –

I/O Connectors	2 Pin 5.08 mm pitch pluggable screw Terminal Block with max 2.5 sq mm wire connection.

Dimensions			110 mm B x 110 mm L x 50 mm H

Power			Input Power – 12 – 24 VDC or 24 V AC/DC

Typical – 12V DC @ 500mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

Relay Output –

Channels			8

Contact Form		1A, 1C

Contact Material		Ag Alloy

Contact Capacity		10A @ 240VAC, 10A @ 28VDC

Coil Voltage			5 – 48 VDC

Coil Power			0.36 W

Insulation Resistance	250M

Electrical Life		1 x 10^5

Mechanical Life		1 x 10^7

Operating Time 		7 msec, Max 15 msec

Release Time		2 msec, Max 6 msec

Configuration Settings: -

Communication Speed 	10/100 Base-T Ethernet compatible Interface

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID	Configured through web App (Details provided with Product)

Function code DO		0x05 and 0x0F (5 Single coil & 15 multiple coil)

DO Register Address	0,1,2,3,4,5,6,7,8

## Configuration Guide – Ethernet Modbus TCP/IP IO Module:-

- Open a web browser (Google Chrome, Microsoft Edge, Firefox, etc.).

- In the browser’s address bar, type the default IP address:
      192.168.0.160

- Press Enter. A message will appear saying:
      “Please go to http://192.168.0.160/setup.”

- Copy this link (http://192.168.0.160/setup) and paste it into a new browser tab.

- Press Enter again to open the Setup / Configuration Page of the device.

## To Reset the Device to Default Settings

- Place the jumper on the designated Reset position on the device.

- Press the Reset button once.

- The module will reboot and revert to its default IP address: 192.168.0.160.

## To Change the IP Address

- On the Setup / Configuration Page, enter the new IP address you wish to assign.

- Click Submit to save the new settings.

- The device will automatically apply the new IP address.

Note:

- Ensure your PC’s IP address is in the same network range (for example,       192.168.0.xxx) when accessing the module.

8 DOME

After changing the IP, you must use the new address to log in again.

DO

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

L

O

A

D

N

P

- Digital Output (DO) operation: Each channel provides two terminals: C (Common) and NO (Normally Open). When the relay coil is energized, terminal C is internally connected to NO, allowing current to flow. When the relay is de-energized, the connection between C and NO remains open, and the load stays OFF.

- Load Wiring Connections:

  - AC Load Connection: The AC Live (Phase) wire should be connected to terminal C. The load is connected between terminal NO and Neutral (N).

  - DC Load Connection: The positive supply (+V) should be connected to terminal C. The load is connected between terminal NO and Ground (GND).

- Crucial Safety Recommendation and Rating: It is strongly recommended to switch the Live (Phase) conductor in AC applications to ensure the load is safely de-energized when the relay is off.

Note: Ensure that the connected load does not exceed the relay’s contact rating of 10A @ 250VAC (or 10A @ 125VAC) or 10A @ 30VDC (or 10A @ 28VDC).

Module Details –

I/P Power 24 V DC

DO1       DO2      DO3       DO4

RESET SW

Modbus TCP Port

DO8       DO7      DO6       DO5

For more details:  http://www.youtube.com/@wittelb

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805