Technical Datasheet IO Modules with Modbus RTU Protocol with RS485 Interface

The I/O modules communicate via RS485. The port can drive distances up to max 700 meters without the use of any repeater (this feature however also depends on the signal strength of the Modbus Master Device).

The RS485 Digital Sensor module is sturdy, low power usage and easy to use.

2 PT100/1000-2 Thermocouple Module:-

Our Multi-Channel Temperature Measurement System is a versatile and high-precision solution designed for diverse temperature sensing needs. The system integrates Modbus RS485 communication for robust and reliable data transmission. With dual channels for RTD (PT100/PT1000) measurement and dual channels for thermocouple measurement, this device is ideal for industrial, commercial, and scientific applications requiring precise temperature monitoring and remote data access.

Dual RTD Channels:-

- Features two channels for RTD measurements, capable of reading both PT100  and PT1000 sensors.

- Utilizes advanced analog-to-digital conversion technology for accurate and reliable temperature readings.

Dual Thermocouple Channels:-

- Includes two channels for thermocouple measurements, compatible with various thermocouple types (K, J, N, R, S, T, E, B).

- Ensures precise temperature monitoring across a wide range of applications.

- The I/O modules are housed in a DIN rail mountable casing with exposed connectors and LED indicators for easy status monitoring. The DIP switches for setting the Slave ID and Baud rate are conveniently located inside the enclosure.

- The modules feature resettable fuses to protect against reverse polarity connections on both the power and communication ports, ensuring safety and reliability.

Specifications

General:-

Connectors	                       2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions			70 mm L x 110 mm B x 50 mm H

Power			            Input Power – 24 V AC/DC

Typical – 12V DC @ 80mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	           -20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

AI Inputs:-

Channels			4

Input Signal		2–PT100/PT1000–(jumper selectable)-Two wire/Three wire

2–Thermocouple – (K, J, N, R, S, T, E, B).

Accuracy	                       Total Accuracy over All Operating Conditions: 0.5NC

(0.05% of Full Scale) max.

Input Resolution	15-Bit ADC Resolution for PT’s And 19-Bit ADC

Resolution for Thermocouple.

Isolation			Optically Isolated.

Additional Features:-

Communication port isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Configuration Settings:-

Communication Speed 	9600 – 19200 Kbps (DIP SW Selectable)

Data Bits			           8

Parity 			           None

Stop bit			           1

CRC				Yes

Slave ID			           1-15 (DIP SW Selectable)

Function Code		           0x03 Read Holding Registers

AI Register Address	           0,1,2,3

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 0 | RTD1 | 40001 | 0X03 | RS485 | 16 Bit Unsigned int |
| 1 | RTD2 | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 2 | THR1 | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 3 | THR2 | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |

Recommended Cable Electrical Characteristics:-

22 AWG Cable 		                                  Shielded and twisted pair should be used

Tinned Copper		                                   Recommended

Nominal Conductor DCR	                       14.7 ohm / 1000 ft

Nominal Capacitance	                                  11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

## Note:-

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

BAUD RATE DESCRIPTION:-

LSB

MSB

- For Baud rate Selection, DIP SW is used as per the diagram.

- Pulling up the switch will make Baud rate active.

- If no selection is made 9600 will be default Baud rate.

- When you change the Baud rate in the Module power ‘ON’ condition,

please press the reset button to get Change to affect.

| Baud Rate | DIP SWITCH |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |
| 9600 | OFF | OFF | OFF | OFF |
| 19200 | OFF | OFF | OFF | ON |
| 38400 | OFF | OFF | ON | OFF |
| 57600 | OFF | ON | OFF | OFF |
| 115200 | ON | OFF | OFF | OFF |

SLAVE ID DESCRIPTION:-

MSB

LSB

- For Slave ID Selection SW is used to Set The SLAVE ID .

- For Slave ID DIP Switch LSB is “1” follow through “4” is MSB.

- Slave ID Confirmed through below Device ID table .

- IF Eg. Slave ID 1 is Needed to be selected Switch number 1 should pulled up other    three should be selected down side. So”1 0 0 0” will be selected as Slave ID 1.

| Slave ID | DIP SWITCH |  |  |  | OUTPUT (Binary) | OUTPUT (Decimal) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 |  |  |
| 0 | OFF(0) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 1 | ON(1) | OFF(0) | OFF(0) | OFF(0) | 0 0 0 1 | 1 |
| 2 | OFF(0) | ON(1) | OFF(0) | OFF(0) | 0 0 1 0 | 2 |
| 3 | ON(1) | ON(1) | OFF(0) | OFF(0) | 0 0 1 1 | 3 |
| 4 | OFF(0) | OFF(0) | ON(1) | OFF(0) | 0 1 0 0 | 4 |
| 5 | ON(1) | OFF(0) | ON(1) | OFF(0) | 0 1 0 1 | 5 |
| 6 | OFF(0) | ON(1) | ON(1) | OFF(0) | 0 1 1 0 | 6 |
| 7 | ON(1) | ON(1) | ON(1) | OFF(0) | 0 1 1 1 | 7 |
| 8 | OFF(0) | OFF(0) | OFF(0) | ON(1) | 1 0 0 0 | 8 |
| 9 | ON(1) | OFF(0) | OFF(0) | ON(1) | 1 0 0 1 | 9 |
| 10 | OFF(0) | ON(1) | OFF(0) | ON(1) | 1 0 1 0 | 10 |
| 11 | ON(1) | ON(1) | OFF(0) | ON(1) | 1 0 1 1 | 11 |
| 12 | OFF(0) | OFF(0) | ON(1) | ON(1) | 1 1 0 0 | 12 |
| 13 | ON(1) | OFF(0) | ON(1) | ON(1) | 1 1 0 1 | 13 |
| 14 | OFF(0) | ON(1) | ON(1) | ON(1) | 1 1 1 0 | 14 |
| 15 | ON(1) | ON(1) | ON(1) | ON(1) | 1 1 1 1 | 15 |

NOTE:-By default, the Jumper setting on the board is PT100.

THR2  THR1        AI1

RTD1   RTD2        AI4

Input12-24 VAC/DC

Modbus RS 485

Slave ID

Baud Rate

Jumper

PT100/PT1000

Jumper

2/3 Wire

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi, Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805