Technical Datasheet RS485 Display

RS485 Display - Module: -

This digital LED display is designed for precise industrial data visualization. With RS485 communication and Modbus RTU support, it can interface directly with PLCs and automation systems. The display shows real-time process parameters and allows configuration of settings such as baud rate, parity, and slave ID. Its durable design ensures reliable performance in demanding industrial conditions.

Specifications

General –

I/O Connectors	 2 Pin pitch pluggable screw terminals.

Dimensions			  7.6 x 3.92 x 2.15 cm

Power			  Input Power – 12 – 24 VDC

Typical – 12V DC @ 80mA

Operating Temperature 	  0 – 60 C (32 ~ 140F)

Storage Temperature	 -20 - 70 C (-4 ~ 158F)

Storage Humidity		  5 ~ 95 % RH, non – Condensing

Certifications

Display Specification:

Type			 7 Segment/ 14-Segment.

Digit Count               4 Digit.

Digit Height              0.56 inch / 0.14mm.

Color                       	  Red.

Update Rate           	  1Hz.

Enclosure Size	   70mm x 40mm x 20mm (direct mountable in slot)

Additional Features: -

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

Configuration Settings: -

Communication Speed 	9600 – 19200 Kbps (Soft Serial)

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID			1-247

Function Code 		0x03 Read Holding Registers

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

RS485 Display Register:-

- First Register – Value to Display

- Purpose: Write the actual number you want to show on the display.

- Type: Usually a single holding register (16-bit).

- Example:

- If you want to display 1234, write 1234 to this register.

- Note: The display will update immediately when the value is written.

- Second Register – Decimal Point Selection

- Purpose: Control where the decimal point appears on the display.

- Type: Usually another holding register (16-bit).

- Example:

  - 0 → no decimal

  - 1 → 1 decimal place (e.g., 123.4)

  - 2 → 2 decimal places (e.g., 12.34)

  - 3 → 3 decimal places (e.g., 1.234)

- Note: Some displays use bitmasking, where each bit represents a DP position. Always check the datasheet.

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 0 | Display Number | 40001 | 0X03 | RS485 | 16 Bit Unsigned int |
| 1 | Decimal Point | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 2 |  | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 3 |  | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 4 |  | 40005 | 0x03 | RS485 | 16 Bit Unsigned int |
| 5 |  | 40006 | 0x03 | RS485 | 16 Bit Unsigned int |
| 6 |  | 40007 | 0X03 | RS485 | 16 Bit Unsigned int |
| 7 |  | 40008 | 0X03 | RS485 | 16 Bit Unsigned int |
| 8 |  | 40009 | 0x03 | RS485 | 16 Bit Unsigned int |
| 9 |  | 40010 | 0x03 | RS485 | 16 Bit Unsigned int |
| 10 | Display Baud Rate (Default:960) | 40011 | 0X03 | RS485 | 16 Bit Unsigned int |
| 11 | Enter New Baud Rate | 40012 | 0X03 | RS485 | 16 Bit Unsigned int |
| 12 | Display Slave ID (Default:1) | 40013 | 0X03 | RS485 | 16 Bit Unsigned int |
| 13 | Enter New Slave ID | 40014 | 0x03 | RS485 | 16 Bit Unsigned int |
| 14 | Display Parity (Default: None-3And for Odd-1,Even-2) | 40015 | 0x03 | RS485 | 16 Bit Unsigned int |
| 15 | Enter New Parity | 40016 | 0x03 | RS485 | 16 Bit Unsigned int |
| 16 | Display Stop Bit (start-2/stop bit-1) | 40017 | 0x03 | RS485 | 16 Bit Unsigned int |
| 17 | Enter New Start/ Stop Bit | 40018 | 0x03 | RS485 | 16 Bit Unsigned int |

Note:

- In register 40015- you will able to see the current parity and you can change it in register 40016

- In register 40017- you will able to see the current stop bit and you can change it in register 40018

- If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it as 960/1920/5760/11520etc.

- After that press the reset button or reboot the system.

BAUD RATE and SLAVE ID DESCRIPTION:

As you can see in the image above, the resistor 40011 – 960 represents the present bund rate (9600) of the board and 40013 – 1 represents the present slave id of the board.

To change the baud rate and slave id you have to enter a value on the 40012 resistor for the baud rate and 40014 for the slave id as shown in the image below.

As you can see in the image above I set 115200 baud rate and slave ID 25.

Note:

1. If you want to enter the baud rate 9600/19200/38400/57600/115200etc.

Enter it like this 960/1920/5760/11520etc.

2. After that press the reset button or reboot the system.

3. Then you will get the present value of 11520 at 40011 baud rate(115200) and 25 at 40013 slave id.

4.  You can Change Parity Bit , stop bit Of the device with same way.

Resetting Modbus Setting

- To restore the device to its default Modbus settings:

- Pull out the jumper as shown in the image.

- Press the reset button while the jumper is removed.

- Release the reset button.

- Re-insert the jumper (if required).

- Note: This will restore all Modbus settings (ID, baud rate, parity, etc.) to factory defaults. Any custom configuration will be lost.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

Reset

Jumper

Modbus RS 485

Input12-24 VDC

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805