Technical Datasheet Input / Output Modules with Modbus RTU Protocol with RS485 Interface

8DDAPM Module: -

The RS485 IO module is a compact, robust, and low-power device designed for reliable communication over distances up to 700 meters without a repeater, depending on the signal strength of the Modbus master. It features 8 digital inputs, 8 digital outputs, 8 analog inputs (10-bit resolution, supporting 0–20 mA and 0–10 V), and 8 RTD (PT1000) channels, making it ideal for versatile industrial applications. Housed in a DIN rail-mountable enclosure, the module includes exposed connectors for easy wiring and LED indicators for real-time I/O status monitoring. Configuration of slave ID and baud rate is done via internal DIP switches. To enhance system protection, the module is equipped with resettable fuses guarding against reverse polarity on both power and RS485 communicatio

Specifications

General –

I/O Connectors	2 Pin 5.08 mm pitch pluggable screw terminals.

Dimensions			155 mm L x 110 mm B x 75 mm H

Power			Input Power – 12 - 24 VDC

Typical – 12V DC @ 120mA

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

DI Inputs –

Channels			8

Sense Voltage 		3.3 – 30 VDC

Sense Logic			Logic ‘0’ = <1 VDC, Logic ‘1’ = >3.3 VDC

Isolation			Optically isolated

Response Time		2 msec, Max 6 msec

Digital Output

Channels			8

Output Type 		P-Channel MOSFET

Channel Voltage		12 VDC/24 VDC

Channel Current               20A

Channel Power		 240 W (max)

Operating Time 		 2.8ns.

Turn Off delay Time          33.5ns.

Operating Temperature   -55℃~+150

AI Inputs –

Channels			8

Input Signal			4 – 20 mA / 0 – 10VDC

Accuracy			 2% Full scale

Input Resolution		10 bits

Isolation			Optically Isolated

External Loop Voltage	+ 12 VDC min

AI input impedance 	120

AI Inputs –

Channels			8– PT1000 – (jumper selectable) three wire

Accuracy	                       Total Accuracy over All Operating Conditions: 0.5NC

(0.05% of Full Scale) max.

Input Resolution		15-Bit ADC Resolution.

Isolation			Optically Isolated.

Additional Features: -

All inputs  and communication ports isolated

Input power reverse polarity safety

ESD Safety IEC 61000-4-2,  30KV contact,  30KV air

EFT IEC 61000-4-4, 50A (5/50ms)

750V isolation.

CRC Error check.

No configuration needed on the IO board

Configuration Settings: -

Communication Speed 	9600 – 115200 (DIP SW selectable)

Data Bits			8

Parity 			None

Stop bit			1

CRC				Yes

Slave ID			Configurable with DIP Switch

Function code DO		0x05 and 0x0F (5 Single coil & 15 multiple coil)

DO Register Address	0,1,2,3,4,5,6,7.

Function code DI		0x02 Read discrete Input

DI Register Address	8, 9,10,11,12,13,14,15.

Function Code AI		0x03 Read Holding Registers

AI Register Address	10 Bit – 1, 2, 3, 4, 5, 6, 7, 8.

RTD Register Address       9, 10, 11, 12, 13,14,15,16.

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | DO 1 | 00001 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 2 | DO 2 | 00002 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 3 | DO 3 | 00003 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 4 | DO 4 | 00004 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 5 | DO 5 | 00005 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 6 | DO 6 | 00006 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 7 | DO 7 | 00007 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 8 | DO 8 | 00008 | 0X05,0X0F | RS485 | 1 Bit Boolean |
| 9 | DI 1(With & Without Potential) | 10009 | 0X02 | RS485 | 1 Bit Boolean |
| 10 | DI 2(With & Without Potential) | 10010 | 0X02 | RS485 | 1 Bit Boolean |
| 11 | DI 3(With & Without Potential) | 10011 | 0X02 | RS485 | 1 Bit Boolean |
| 12 | DI 4(With & Without Potential) | 10012 | 0X02 | RS485 | 1 Bit Boolean |
| 13 | DI 5(With & Without Potential) | 10013 | 0X02 | RS485 | 1 Bit Boolean |
| 14 | DI 6(With & Without Potential) | 10014 | 0X02 | RS485 | 1 Bit Boolean |
| 15 | DI 7(With & Without Potential) | 10015 | 0X02 | RS485 | 1 Bit Boolean |
| 16 | DI 8(With & Without Potential) | 10016 | 0X02 | RS485 | 1 Bit Boolean |
| 17 | AI 1 | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 18 | AI 2 | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |
| 19 | AI 3 | 40004 | 0X03 | RS485 | 16 Bit Unsigned int |
| 20 | AI 4 | 40005 | 0X03 | RS485 | 16 Bit Unsigned int |
| 21 | AI 5 | 40006 | 0X03 | RS485 | 16 Bit Unsigned int |
| 22 | AI 6 | 40007 | 0X03 | RS485 | 16 Bit Unsigned int |
| 23 | AI 7 | 40008 | 0X03 | RS485 | 16 Bit Unsigned int |
| 24 | AI 8 | 40009 | 0X03 | RS485 | 16 Bit Unsigned int |
| 25 | RTD1 1000 | 40010 | 0X03 | RS485 | 16 Bit Unsigned int |
| 26 | RTD2 1000 | 40011 | 0X03 | RS485 | 16 Bit Unsigned int |
| 27 | RTD3 1000 | 40012 | 0X03 | RS485 | 16 Bit Unsigned int |
| 28 | RTD4 1000 | 40013 | 0X03 | RS485 | 16 Bit Unsigned int |
| 29 | RTD5 1000 | 40014 | 0X03 | RS485 | 16 Bit Unsigned int |
| 30 | RTD6 1000 | 40015 | 0X03 | RS485 | 16 Bit Unsigned int |
| 31 | RTD7 1000 | 40016 | 0X03 | RS485 | 16 Bit Unsigned int |
| 32 | RTD8 1000 | 40017 | 0X03 | RS485 | 16 Bit Unsigned int |

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

Connection Instruction FOR WIN - IO – 8DDAPM

H2

H1

Note:

      - Identify the AI/PT1000 wiring, configuration, or specification

      - For AI there are 2 Jumpers Eg. Jumper “H1” & “H2” are for Selecting the Input Voltage Detection. + & - Terminal are used for all AI INPUT
The system supports monitoring of both Analog Input (AI) and RTD (PT1000) sensor data.

      - Selection between AI and RTD input modes is achieved by configuring the appropriate jumper settings. Refer to the provided diagram for correct jumper positions and wiring connections.

      - Ensure that only one mode is selected at a time to prevent signal conflict or inaccurate readings.

      - H1 is for selection of analog input and RTD(PT1000)

      - H2 is for voltage selection between 5V and 10V.

DI

I/p device

I/p device

I/p device

I/p device

- Operation: The module provides four isolated input channels (DI1–DI4) for sensing external signals or dry contacts. These inputs are opto-isolated for circuit protection.

- Terminal Layout:

  - GND: Common Ground reference.

  - DI1 – DI4: Individual Digital Input channels.

  - +12V: Internal reference voltage for sourcing "Dry Contact" switches.

- Wiring Options:

  - Dry Contact: Connect a switch between the +12V terminal and any DI pin.

  - External Voltage: Connect the external signal to a DI pin and the external ground to the GND terminal.

- Voltage Rating: The input circuitry is rated for a maximum of 80VDC. Ensure external signals do not exceed this limit to prevent damage to the isolation ICs.

BAUD RATE DESCRIPTION

LSB

MSB

- For Baud rate Selection, DIP SW is used as per the diagram.

- Pulling up the switch will make Baud rate active.

- If no selection is made 9600 will be default Baud rate.

- When u change the Baud rate in the Module power ‘ON’ condition,

pls press the reset button to get Change to affect.

SLAVE ID DESCRIPTION

MSB

LSB

For Slave ID Selection SW is used to Set The SLAVE ID .

For Slave ID DIP Switch LSB is “1” follow through “5” is MSB.

Slave ID Confirmed through below Device ID table .

IF Eg. Slave ID 1 is Needed to be selected Switch number 1 should pulled up other three should be selected down side. So”0 0 0 0 1” will be selected as Slave ID 1.

### Slave ID Configuration

The slave ID can be configured as per user preference using a 5-bit DIP switch setting. The binary value set by the switches corresponds to a specific decimal slave ID.

| Binary (DIP Switch) | Decimal Slave ID |
| --- | --- |
| 00001 | 1 |
| 10000 | 16 |
| 11111 | 31 |

Note:

- Bit position and value mapping may vary based on hardware implementation (e.g., LSB ↔ MSB). Refer to the device’s DIP switch bit order specification when setting the ID.

- DIP switches SW1 to SW5 are provided for user configuration. These switches can be set as per the application requirements to control functions such as slave address selection, mode settings, or other device parameters.

- The device supports configurable slave addresses within the range of 1 to 31, which can be set according to application requirements.

Common

GND

1     2    3     4    5      6     7    8

AI / PT 1000 Channel

Modbus RS485

5V/10V

Jumper

AI/PT

Jumper

SLAVE    ID

BAUD RATE

DI8 DI7 DI6 DI5 DI4 DI3 DI2 DI1

DI Channel

DO8 D07 DO6 DO5 DO4 DO3 DO2 DO1

DO Channel

Input 12-24    VDC

+12/24V Reference Voltage

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805