Technical Datasheet of WIN-PiHAT-8AO

1. Overview

The Analog Output (AO) PiHAT is an 8-channel expansion board for Raspberry Pi 4 and CM4, offering high-resolution analog outputs for industrial control systems. It provides precise signal generation by supporting both 12-bit and 16-bit data resolution, ensuring accurate 0-10V control signals are delivered from the Pi to external analog devices (such as VFDs and proportional valves) for reliable operation in industrial environments.

This PiHAT features a scalable architecture supporting 1 to 8 independent analog outputs (AO). Its population-based design allows channel flexibility while maintaining a compact and reliable solution for embedded control, automation, and precise industrial driving applications.

Specifications

| Category | 8AO PiHAT |
| --- | --- |
| Output Type | High-Resolution Analog Outputs, Selectable 12-bit or 16-bit DAC Resolution (0-10V Range) |
| Channel Count | 8 Channels (Expandable Design Architecture) |
| Connectors | 2.54 mm Pluggable Terminal Blocks (for sensor inputs), 40-Pin Raspberry Pi GPIO Header |

General :–

Dimensions			56 mm L x 85 mm W

Power			Input Power – 12/24V DC

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

AO (Analog Outputs) :–

Channels			8

DAC Resolution		12-bit / 16-bit (Selectable)

Output Type		Single-Ended Voltage Output

Voltage Output Range	0 ~ 10V DC

Max Output Current	35 mA (Short-Circuit limit), ~15 mA continuous

Input Impedance(I)	~ 250 Ω (Typical for mA drop)

Accuracy			±0.1% to ±0.3% FSR (Full Scale Range)

Settling Time		14 µs (Typical)

Protection			Short-circuit protection to ground

Configuration :-

All 8 AO channels operate as high-resolution analog outputs and are interfaced to the Raspberry Pi GPIO header through an onboard Digital-to-Analog Converter (DAC) IC. Signal generation is managed via software running on the Raspberry Pi. Each channel is configured to continuously hold and drive outgoing analog signals to external industrial equipment.

When a precise digital value (using either 12-bit or 16-bit resolution) is computed by your software, the Raspberry Pi transmits this data over the SPI communication bus to the DAC. The DAC processes this digital command and immediately converts it into a continuous, proportional analog voltage (0-10V) at the designated output terminal, allowing your software to accurately drive proportional valves, VFDs, and other real-world actuators.

The following are step by step guides for configuration:

- Connect the Module to +12/24V DC POWER SUPPLY.

- Connect the Board to the Raspberry Pi via header pins

| Bus Type | Signal Name | Pi GPIO | Header Pin Number | Description |
| --- | --- | --- | --- | --- |
| SPI | MOSI | 10 | 19 | SPI data line for TCP112S8 & TCP116S8 |
|  | MISO | 09 | 21 |  |
|  | SCLK | 11 | 23 |  |
|  | CE0/CS | 08 | 24 |  |
|  | CE1/CS` | 07 | 26 |  |

AO1-8

GND

Wiring Diagram:-

- Analog Output (AO) Operation: Each channel provides two terminals: + (Positive) and - (Negative/Common). These are used to deliver generated analog control signals to external devices.

- Channel Configuration (Visual Guide): Each of the AO channels features a dedicated jumper to independently set the bit resolution. The output voltage range is fixed at a maximum of 10V.

  - Resolution Selection: Place the resolution jumper on the 12-bit position for standard control applications, or on the 16-bit position for high-precision signal generation.

- Device Wiring Connections:

  - The receiving device's (e.g., VFD, proportional valve) positive signal input wire should be connected to the + terminal of the desired channel.

  - The device's common or ground reference wire should be connected to the corresponding - terminal.

- Crucial Setup Recommendation: Because the board outputs a fixed 0-10V control signal, always ensure your connected industrial equipment is rated to safely accept up to 10V. Double-check your terminal polarity before sending digital-to-analog (DAC) commands to prevent damage to sensitive receiving inputs.

Sample Test Code:  WIN-PiHAT-8AO

Hardware Interface & Connector Layout:

40 pin GPIO Headers

12/16 BIT JUMPER

12/24V DC SPLY

AO1      AO2      AO3      AO4       AO5       AO6       AO7                      AO8

ANALOG OUTPUT

2

1

40

39

POWER LED

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805