Technical Datasheet TnH Sensor Modules with Modbus RTU

Protocol with RS485 Interface

The SN modules communicate via RS485. The port can drive distances up to max

700 meters without the use of any repeater (this feature however also depends

on the signal strength of the Modbus Master Device).

The RS485 SN-TnH module is sturdy, has low power usage and is easy to use.

TnH Sensor Module: -

The SN modules can be mounted in Outdoor or Indoor environment. Soft setting for Slave ID is available in the software. In Addition, it has reset switch for Slave ID reset if forgotten.

The design of the modules incorporates ‘resettable Fuses’ to safeguard against reverse polarity connection both for Power and Communication port.

Specifications

General –

Dimensions			158mm L x 139 mm D

Power			Input Power – 12 - 24 V DC

Operating Temperature	0 – 60 C (32 ~ 140F)

Storage Temperature	-20 - 70 C (-4 ~ 158F)

Storage Humidity		5 ~ 95 % RH, non – Condensing

Certifications

Configuration Settings: -

Communication Speed 	9600

Data Bits			8

Parity 			None

CRC				Yes

Slave ID			Software setting(1-247)

| ID | Function Description | Register Description | Modbus Function Code | Protocol | Data Type |
| --- | --- | --- | --- | --- | --- |
| 1 | Temperature | 40000 | 0X03 | RS485 | 16 Bit Unsigned int |
| 2 | Humidity | 40001 | 0X03 | RS485 | 16 Bit Unsigned int |
| 3 | Current Slave ID | 40002 | 0X03 | RS485 | 16 Bit Unsigned int |
| 4 | Enter New Slave ID | 40003 | 0X03 | RS485 | 16 Bit Unsigned int |

Note: -

For MODBUS communications, a shielded and twisted pair cable is used. One example of such cable is Belden 3105A.

Recommended Cable Electrical Characteristics: -

22 AWG Cable 				Shielded and twisted pair should be used.

Tinned Copper				Recommended

Nominal Conductor DCR			14.7 ohm / 1000 ft

Nominal Capacitance			11 pf / feet (conductor to conductor)

High Frequency Non-Insertion Loss	0.5db / 100ft

- Here is an example of receiving data on Mb poll software.

- Open Mb-poll software connect using configuration setting (Fixed baud rate is 9600 and Default slave id is 1.

- After connecting you will get data as shown below

- As you can see in the image above, the resistor 40002 –1 represents the present slave ID of the module

- To change the slave id, you must enter a value on the 40003 resistor for the new slave id as shown in the image.

- After that the slave ID will be changed.

- Somehow you forgot the slave id of the board, in that case press reset button and remove power supply. Then you will get the default slave ID 1 for the system.

| Sensor Name | Temperature Measuring Range | Humidity Measuring range | Operating Temperature | Measuring Accuracy |
| --- | --- | --- | --- | --- |
| AHT20 | -20°C ~ 85°C. | 0~100% RH. | -40°C ~ 120°C. | 0.3°C, 2.0 %RH |
| AHT21 | -40°C ~ 120°C. | 0~100% RH. | -40°C ~ 120°C. | 0.3°C, 2.0 %RH |

Contact us: -

Augmatic Technologies Pvt. Ltd.,

Plot no 6, Shah Industrial Estate II,

Kotambi,

Vadodara – 391510.

Email – Sales@wittelb.com

Support: support@wittelb.raiseaticket.com  / +91 94038 92805